## Yearly Summary
2016 |  | BWPF Yearly Summary Chem Flow Total Report
|  | South Platte Chemicals | [6 empty] | Aurora Reservoir Chemicals | [5 empty] | Filter Adsorber Chemicals | [5 empty] | Finished Water Chemicals | [6 empty] | Miscellaneous Chems |  | Raw Flow To Process |  |  | Finished Flows (MG) & Ratios
|  | KMnO4 (RW) | FeCl3 (RM & Flow Split) | NaOH (Rapid Mix) | PEC/PEA (Reactors) | PEA (Sludge) | CO2 (Post Softening) | H202 (UV) | KMnO4 (RW) | FeCl3 (Rapid Mix) | PEC (Rapid Mix) | PAC (Basin 1 & 2) | PEA (Basin 1 & 2) | PEA (Sludge) | PEN AR (FIC) | PEN SP (FIC) | PEN AR (Ind Filters) | PEN SP (Ind Filters) | FeCl3 AR Filter Backwash | FeCl3 SP Filter Backwash | Cl2 AR | Cl2 SP | NH3 AR (CCB Effluent) | NH3 SP (CCB Effluent) | NaOH AR (CCB Effluent) | NaOH SP (CCB Effluent) | Fluoride(CCB Effluent) | From Chlorinator 5 | Wemlinger AR (VV1) | RWAR To Process | RWSP To Process |  | Finished Water Flow | AR Net to Distribution | SP Net to Distribution | AR to Total Flow Blend
Monthly Flow Totals | January | 0 | 2318.9901 | 25054.4517 | 900.9351 | 0 | 60893.9488 | 825.7742 | 3435.9604 | 10554.9931 | 573.6992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6662.1189 | 4898.44 | 972.1772 | 714.4634 | 2026.8769 | 1488.3344 | 0 | 1845.9791 | 0 | 259.7306 | 188.2218 | 447.9524 | 431.6341 | 245.5894 | 180.5737 | 0.57628
| February | 0 | 1681.307 | 21898.8866 | 734.3348 | 0 | 56741.2257 | 744.9471 | 3052.6796 | 9590.8806 | 521.5634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5955.365 | 4325.3449 | 867.1515 | 629.9979 | 1775.4398 | 1289.6793 | 0 | 2018.7447 | 0 | 236.0111 | 169.9692 | 405.9803 | 383.7456 | 219.6428 | 159.6049 | 0.57915
| March | 0 | 1684.5125 | 26658.1268 | 479.1312 | 0 | 94215.3935 | 763.3722 | 3562.1867 | 10740.5801 | 585.0855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7317.6033 | 4361.4844 | 1126.3794 | 673.1715 | 3353.4913 | 1979.29 | 0 | 2349.1781 | 0 | 295.1268 | 178.319 | 473.4458 | 452.1297 | 279.7278 | 167.0341 | 0.62612
| April | 0 | 1881.1812 | 26584.2059 | 477.4179 | 0 | 82389.5601 | 786.5478 | 3842.6239 | 11345.3253 | 622.565 | 0.0022565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7766.757 | 4513.9024 | 1228.3519 | 713.6147 | 3498.1214 | 2031.783 | 0 | 2355.4396 | 0 | 320.5558 | 179.5332 | 500.089 | 488.0625 | 304.5516 | 176.9824 | 0.63246
| May | 0 | 1825.696 | 22105.4339 | 459.4341 | 0 | 51093.5493 | 757.3349 | 6029.9065 | 14121.956 | 773.0748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10002.5635 | 4064.5426 | 1589.3428 | 641.8111 | 4718.171 | 1916.445 | 0 | 2705.6778 | 0 | 420.7266 | 172.6834 | 593.41 | 554.2439 | 402.3399 | 162.7347 | 0.71201
| June | 0 | 1898.6339 | 20824.0569 | 476.5249 | 0 | 40986.1783 | 788.3072 | 6211.369 | 15224.6265 | 827.0448 | 0.00055704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11374.1457 | 4251.3218 | 1804.3133 | 670.991 | 6205.7738 | 2298.8561 | 0 | 3046.8517 | 0 | 477.7445 | 179.5112 | 657.2557 | 636.034 | 457.7684 | 170.3585 | 0.72878
| July | 0 | 2058.254 | 21634.2145 | 518.0246 | 0 | 47610.8433 | 853.5025 | 5239.9612 | 15220.3811 | 832.9886 | 0.00069866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12184.292 | 5115.2721 | 1828.4025 | 763.3991 | 7720.2098 | 3214.1742 | 0 | 3425.047 | 0 | 501.5221 | 203.0353 | 704.5573 | 659.7032 | 459.9381 | 192.0275 | 0.70546
| August | 0 | 3064.8517 | 36828.9646 | 773.9631 | 0 | 61728.6531 | 1164.0171 | 8639.2148 | 25413.377 | 1393.7751 | 0.00041542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18209.1441 | 6681.2151 | 3135.496 | 1144.1556 | 15307.9512 | 5565.2948 | 0 | 5337.1726 | 0 | 799.0986 | 289.3096 | 1088.4083 | 1067.4481 | 772.7573 | 282.3374 | 0.73241
| September | 0 | 3030.933 | 29788.6096 | 624.6029 | 0 | 47287.232 | 936.6112 | 4770.4707 | 10741.8718 | 588.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8059.0008 | 5875.4992 | 1261.9623 | 914.511 | 5156.0217 | 3696.7816 | 0 | 2715.9147 | 0 | 333.4233 | 233.6326 | 567.0558 | 551.584 | 315.6913 | 228.6421 | 0.57996
| October | 0 | 241.6265 | 2801.9138 | 60.2391 | 0 | 4835.7011 | 91.8648 | 4176.9239 | 9411.5112 | 532.6725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6105.8266 | 623.5712 | 887.1326 | 89.5513 | 3156.9955 | 346.762 | 0 | 1653.3756 | 0 | 244.0473 | 22.9636 | 267.0109 | 241.1565 | 216.848 | 22.3271 | 0.90665
| November | 0 | 0 | 0 | 10.9674 | 0 | 0 | 0 | 6350.7541 | 13983.4905 | 835.7387 | 0.12503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8740.8367 | 0 | 1292.8986 | 0 | 4982.5934 | 0 | 0 | 1527.0967 | 0 | 343.8006 | 6.107 | 349.9076 | 327.5537 | 323.2148 | 0 | 1
| December | 0 | 1317.9139 | 18658.5907 | 342.6208 | 0 | 83987.3091 | 424.0015 | 5090.9198 | 12019.7697 | 715.9596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7979.3213 | 2645.9753 | 1185.3453 | 405.6543 | 4538.9278 | 1518.2672 | 0 | 2030.7986 | 0 | 313.543 | 124.0197 | 437.5627 | 399.989 | 294.3965 | 99.8424 | 0.74675
Metered Unit |  | Gallons | Gallons | Gallons | Gallons | Gallons | Pounds | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Pounds | Pounds | Gallons | Gallons | Gallons | Gallons | Gallons | Pounds | Gallons | MGD | MGD | MGD | MGD | MGD | MGD | Ratio
Flow Total | Year | 0 | 21003.8997 | 252837.4551 | 5858.1959 | 0 | 631769.5942 | 8136.2806 | 60402.9706 | 158368.7628 | 8802.2131 | 0.12895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110356.9747 | 47356.569 | 17178.9534 | 7361.3209 | 62440.5736 | 25345.6675 | 0 | 31011.2763 | 0 | 4545.3303 | 1947.3056 | 6492.6359 | 6193.2842 | 4292.4662 | 1842.4648 | 0.69968
Monthly Costs $ | January | 0 | 3446.8421 | 77229.4455 | 3594.6014 | 0 | 3528.8043 | 3087.5951 | 2821.8993 | 15688.4646 | 2288.9774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1995.9708 | 1467.5726 | 722.8082 | 531.1995 | 6247.775 | 4587.7372 | 0 | 553.0553 | 0
| February | 0 | 2499.0188 | 67502.5295 | 2929.8901 | 0 | 3288.154 | 2785.3798 | 2507.1169 | 14255.4514 | 2080.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1784.2273 | 1295.8733 | 644.7222 | 468.3999 | 5472.7292 | 3975.3901 | 0 | 604.8159 | 0
| March | 0 | 2503.7832 | 82172.716 | 1911.6644 | 0 | 5459.7821 | 2854.2721 | 2925.5669 | 15964.3128 | 2334.4068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2192.3539 | 1306.7007 | 837.4567 | 500.4992 | 10337.0163 | 6101.09 | 0 | 703.8137 | 0
| April | 0 | 2796.1027 | 81944.8577 | 2070.4658 | 0 | 4774.475 | 2940.9263 | 3155.8855 | 16863.1787 | 2699.9399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2326.9204 | 1352.3652 | 913.2726 | 530.5685 | 10782.8332 | 6262.8979 | 0 | 705.6897 | 0
| May | 0 | 2713.632 | 68139.2041 | 1992.474 | 0 | 2960.8712 | 2831.6982 | 4952.2657 | 20990.2371 | 3352.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2996.768 | 1217.737 | 1181.6673 | 477.1829 | 14543.5923 | 5907.3727 | 0 | 810.6211 | 0
| June | 0 | 2822.0436 | 64189.4058 | 2066.5933 | 0 | 2375.149 | 2947.5046 | 5101.298 | 22629.1966 | 3586.7277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3407.694 | 1273.696 | 1341.4967 | 498.878 | 19129.0744 | 7086.1411 | 0 | 912.8368 | 0
| July | 0 | 3059.2956 | 66686.6875 | 2246.5691 | 0 | 2855.4603 | 3191.2718 | 4303.4963 | 22622.8865 | 3612.5049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3650.4139 | 1532.5355 | 1359.4069 | 567.5829 | 23797.2689 | 9907.5763 | 0 | 1026.1441 | 0
| August | 0 | 4555.457 | 113523.9576 | 3356.5231 | 0 | 3702.176 | 4352.2954 | 7095.2489 | 37773.2948 | 6044.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5455.4596 | 2001.692 | 2331.2235 | 850.6732 | 47186.2086 | 17154.8209 | 0 | 1599.0169 | 0
| September | 0 | 4505.0418 | 91822.3168 | 2708.7779 | 0 | 2836.0517 | 3502.0179 | 3917.9113 | 15966.2327 | 2550.2371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2414.4766 | 1760.2996 | 938.2618 | 679.9337 | 15893.2512 | 11395.1961 | 0 | 813.688 | 0
| October | 0 | 359.1427 | 8276.9319 | 261.245 | 0 | 290.0212 | 343.4854 | 3430.4408 | 13988.8448 | 2310.0941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1829.3057 | 186.8219 | 659.5781 | 66.5809 | 9325.8531 | 1024.3445 | 0 | 495.3513 | 0
| November | 0 | 0 | 0 | 47.5635 | 0 | 0 | 0 | 5215.7727 | 20784.4283 | 3624.4317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2618.7547 | 0 | 961.2628 | 0 | 14718.7205 | 0 | 0 | 457.5182 | 0
| December | 0 | 1958.8876 | 55117.9993 | 1485.8779 | 0 | 5037.1389 | 1585.3547 | 4181.091 | 17865.6424 | 3104.9736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2390.6047 | 792.7342 | 881.2975 | 301.6017 | 13408.1197 | 4485.0039 | 0 | 608.4272 | 0
Total Cost | Year | 0 | 31219.2472 | 776606.0517 | 24672.2454 | 0 | 37108.0837 | 30421.8013 | 49607.9934 | 235392.1707 | 37590.4512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33062.9496 | 14188.0281 | 12772.4543 | 5473.1003 | 190842.4422 | 77887.5707 | 0 | 9290.9784 | 0
|  | Total | SP | AR
Monthly Costs per KG | January | 0.68024 | 0.99664 | 0.44883
| February | 0.97549 | 1.3367 | 0.71276
| March | 0.93294 | 1.429 | 0.63081
| April | 0.72637 | 1.2002 | 0.45877
| May | 0.65205 | 1.2247 | 0.4151
| June | 0.61462 | 1.2098 | 0.38905
| July | 0.56668 | 1.0652 | 0.3628
| August | 0.6457 | 1.2963 | 0.40814
| September | 0.68462 | 1.0233 | 0.44483
| October | 0.95252 | 5.1315 | 0.55727
| November | 0.7949 | 17.9502 | 0.48883
| December | 1.1632 | 2.1522 | 0.77009
| Average | 0.78245 | 3.0013 | 0.50727
|  | Total | SP | AR
Annual Report Summary | Chemical Cost per MG | 241.2172 | 512.2854 | 123.0424
| Labor Cost per MG | 308.997 | 515.1234 | 220.6886
| O&M Cost per MG | 432.9631 | 721.7849 | 309.2263
| Material Cost per MG | 123.966 | 206.6615 | 88.5377
| Natural Gas Cost per MG | 17.3597 | 23.6665 | 14.6578
| Electrical Cost per MG | 52.1189 | 97.2348 | 32.7903
| Electrical Usage (kWHr) | 5141312.6324 | 2879092.1676 | 2262220.4648
| Electrical Usage per MG | 791.8683 | 1478.5005 | 497.7021
| Total Cost per MG | 743.6588 | 1354.9715 | 479.7169
| Total Cost per KG | 0.74366 | 1.355 | 0.47972
| Total Flow (MG) | 6492.6359 | 1947.3056 | 4545.3303
Note on B50: Peter Bong: Account Series 6,000 with electric and gas bills subtracted

## Projection Instructions
bwpfprofile

## Projection
2019 | BWPF YTD Chemical Usage & Cost
| South Platte Chemicals | [13 empty] | Aurora Reservoir Chemicals | [12 empty] | Miscellaneous Chems |  | 2018 YTD Finished Delivered Flows (MG) & Ratios
| SP Pre-Treatment | [6 empty] | SP Filter/Adsorber |  |  | SP Finished Water |  |  |  | AR Pre-Treatment | [5 empty] | AR Filter/Adsorber |  |  | AR Finished Water
| KMnO4 (RW) | FeCl3 (RM & Flow Split) | NaOH (Rapid Mix) | PEC/PEA (Reactors) | PEA (Sludge) | CO2 (Post Softening) | H202 (UV) | PEN SP (FIC) | PEN SP (Ind Filters) | FeCl3 SP Filter Backwash | Cl2 SP | NH3 SP (CCB Effluent) | NaOH SP (CCB Effluent) | Fluoride SP (CCB Effluent) | KMnO4 (RW) | FeCl3 (Rapid Mix) | PEC (Rapid Mix) | PAC (Basin 1 & 2) | PEA (Basin 1 & 2) | PEA (Sludge) | PEN AR (FIC) | PEN AR (Ind Filters) | FeCl3 AR Filter Backwash | Cl2 AR | NH3 AR (CCB Effluent) | NaOH AR (CCB Effluent) | Fluoride AR (CCB Effluent) | From Chlorinator 5 | Wemlinger AR (VV1) | Finished Water Flow | AR Net to Distribution | SP Net to Distribution | AR to Total Flow Blend
Total Metered Units | Gallons | Gallons | Gallons | Gallons | Gallons | Pounds | Gallons | Gallons | Gallons | Gallons | Pounds | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Pounds | Gallons | Gallons | Gallons | Pounds | Gallons | MG | MG | MG | Ratio
| 0 | 21003.8997 | 252837.4551 | 5858.1959 | 0 | 631769.5942 | 8136.2806 | 0 | 0 | 0 | 47356.569 | 7361.3209 | 25345.6675 | 0 | 60402.9706 | 158368.7628 | 8802.2131 | 0.12895 | 0 | 0 | 0 | 0 | 0 | 110356.9747 | 17178.9534 | 62440.5736 | 0 | 4688.3846 | 0 | 6193.2842 | 4292.4662 | 1842.4648 | 0.69968
Total Dry Tons | 0 | 46.5959 | 811.8358 | 25.4058 | 0 | 315.8848 | 13.478 | 0 | 0 | 0 | 23.6783 | 7.9673 | 81.3824 | 0 | 7.7755 | 351.3316 | 38.1734 | 0.00021362 | 0 | 0 | 0 | 0 | 0 | 55.1785 | 18.5932 | 200.4904 | 0 | 2.3442 | 0 | 2018 YTD Treated Raw Water Flows (MG)
Dry Tons per MG Delivered | 0 | 0.02529 | 0.44062 | 0.013789 | 0 | 0.17145 | 0.0073152 | 0 | 0 | 0 | 0.012851 | 0.0043243 | 0.04417 | 0 | 0.0018114 | 0.081848 | 0.0088931 | 4.9766e-08 | 0 | 0 | 0 | 0 | 0 | 0.012855 | 0.0043316 | 0.046708 | 0 | 0.00054612
Dry Tons per MG Treated | 0 | 0.08946 | 1.5586 | 0.048777 | 0 | 0.60647 | 0.025877 | 0 | 0 | 0 | 0.04546 | 0.015297 | 0.15625 | 0 | 0.0025526 | 0.11534 | 0.012532 | 7.0127e-08 | 0 | 0 | 0 | 0 | 0 | 0.018114 | 0.0061038 | 0.065817 | 0 | 0.00076956
Total Cost YTD | 0 | 31219.2472 | 776606.0517 | 24672.2454 | 0 | 37108.0837 | 30421.8013 | 0 | 0.0012106 | 0.018506 | 14188.0281 | 5473.1003 | 77887.5707 | 0 | 49607.9934 | 235392.1707 | 37590.4512 | 0 | 0 | 0 | 0 | 0 | 0.11861 | 33062.9496 | 12772.4543 | 190842.4422 | 0 | 9290.9784 | 0 | AR Rcycl | 42.1859 | SP Rcycl | 89.3826
| South Platte Total |  |  | 997576.148 | Aurora Reservoir Total |  |  | 568559.5584 | Total Delivered |  | 1566135.7064 |  | Delivered Efficiency |  |  | 178.6% | [13 empty] | Gross AR to Binney | Net AR to Binney | Gross SP to Binney | Net SP to Binney
2020 | BWPF Projected Chemical Usage & Cost
Projected Total Metered Units | Gallons | Gallons | Gallons | Gallons | Gallons | Pounds | Gallons | Gallons | Gallons | Gallons | Pounds | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Gallons | Pounds | Gallons | Gallons | Gallons | Pounds | Gallons
| 0 | 13967.9397 | 168141.0769 | 3895.7969 | 0 | 420137.198 | 5410.7608 | 0 | 0 | 0 | 31492.8993 | 4895.3998 | 16855.2868 | 0 | 53132.9474 | 139307.704 | 7742.7902 | 0.11343 | 0 | 0 | 0 | 0 | 0 | 97074.5525 | 15111.3169 | 54925.3072 | 0 | 4124.0967 | 0
Projected Total Dry Tons | 0 | 30.987 | 539.8842 | 16.8953 | 0 | 210.0686 | 8.9631 | 0 | 0 | 0 | 15.7464 | 5.2984 | 54.1206 | 0 | 6.8397 | 309.0458 | 33.5789 | 0.00018791 | 0 | 0 | 0 | 0 | 0 | 48.5373 | 16.3553 | 176.3597 | 0 | 2.062 | 0
Projected Total Cost | 0 | 20761.3142 | 496693.4491 | 16895.292 | 0 | 25197.7285 | 20230.9995 | 0 | 0 | 0 | 9435.2726 | 474.3642 | 49790.9892 | 0 | 43637.2397 | 207060.6746 | 33578.9324 | 0 | 0 | 0 | 0 | 0 | 0 | 29083.5359 | 1464.2866 | 162250.8954 | 0 | 1235.5794 | 0
| South Platte Total |  |  | 639479.4093 | Aurora Reservoir Total |  |  | 478311.144 | Total Delivered |  | 1117790.5533
Projected Total Delivered (MG): |  | 5001.1 | Projected Total Treated (MG): |  |  | 2907.7818 | Projected Average AR %: |  |  | 0.755 | Projected Average AR Ratio: |  |  | 3.0816 | Projected AR Del (MG): |  |  | 3775.8305 | Projected AR Trt (MG): |  |  | 2195.3752 | Projected SP Del (MG): |  |  | 1225.2695 | Projected SP Trt (MG): |  | 712.4065 | MG | MG | MG | MG
[30 empty] | 3046.1644 | 3003.9785 | 520.859 | 431.4764
2020 | Total Projected by Chemical | [6 empty] | Transportation Units | [7 empty] | 2019 | Pricing |  | Quarterly Vendor Unit Pricing |  |  |  |  | Quarterly Metered Unit Pricing |  |  |  |  | Quarterly Dry Ton Pricing
Chemical | Total By Dry Ton |  | Total Dry Ton Cost |  | Total By Vendor Priced Unit |  |  | Partial Trucked Units |  |  | Whole Trucked Units |  | Whole Unit Cost |  |  | Chemical |  |  | Unit | Jan | Apr | July | Oct | Unit | Jan | Apr | July | Oct | Unit | Jan | Apr | July | Oct
Ammonia | 21.6537 |  | 1938.6508 |  | 20006.7167 |  | Liquid Gal | 5.531 |  | Truck Ld | 6 |  | 2103.0505 |  |  | Ammonia |  |  | Liquid Lb | 0.0969 | 0.0969 | 0.0969 | 0.0969 | Liquid Gal | 0.74349 | 0.74349 | 0.74349 | 0.74349 | Dry Ton | 89.5296 | 89.5296 | 89.5296 | 89.5296
Anionic Polymer | 0 |  | 0 |  | 0 |  | Liquid Lb | 0 |  | Tote | 0 |  | 0 |  |  | Anionic Polymer |  |  | Liquid Lb |  |  |  |  | Liquid Gal | 0 | 0 | 0 | 0 | Dry Ton | 0 | 0 | 0 | 0
Carbon Dioxide | 210.0686 |  | 25197.7285 |  | 210.0686 |  | Liquid Ton | 10.5034 |  | Truck Ld | 11 |  | 26389 |  |  | Carbon Dioxide |  |  | Liquid Ton | 115.9 | 115.9 | 119.95 | 119.95 | Liquid Lb | 0.05795 | 0.05795 | 0.059975 | 0.059975 | Dry Ton | 115.9 | 115.9 | 119.95 | 119.95
Carbon PAC | 0.00018791 |  | 0 |  | 0.37581 |  | Dry Lb | 8.3514e-06 |  | Truck Ld | 1 |  | 0 |  |  | Carbon PAC |  |  | Dry Lb |  |  |  |  | Liquid Gal | 0 | 0 | 0 | 0 | Dry Ton | 0 | 0 | 0 | 0
Cationic Polymer | 50.4742 |  | 50474.2244 |  | 50.4742 |  | Liquid Ton | 2.2433 |  | Truck Ld | 3 |  | 67500 |  |  | Cationic Polymer |  |  | Liquid Ton | 920 | 1000 | 1000 | 1000 | Liquid Gal | 3.9899 | 4.3368 | 4.3368 | 4.3368 | Dry Ton | 920 | 1000 | 1000 | 1000
Chlorine | 66.3458 |  | 39754.3879 |  | 66.3458 |  | Liquid Ton | 8.2932 |  | Truck Ld | 9 |  | 43142.4 |  |  | Chlorine |  |  | Liquid Ton | 599.2 | 599.2 | 599.2 | 599.2 | Liquid Lb | 0.2996 | 0.2996 | 0.2996 | 0.2996 | Dry Ton | 599.2 | 599.2 | 599.2 | 599.2
Ferric Chloride | 340.0328 |  | 227821.9888 |  | 340.0328 |  | Dry Ton | 39.7699 |  | Truck Ld | 40 |  | 229140 |  |  | Ferric Chloride |  |  | Dry Ton | 670 | 670 | 670 | 670 | Liquid Gal | 1.4864 | 1.4864 | 1.4864 | 1.4864 | Dry Ton | 670 | 670 | 670 | 670
Hydrogen Peroxide | 8.9631 |  | 20230.9995 |  | 25.6089 |  | Liquid Ton | 1.1382 |  | Truck Ld | 2 |  | 35550 |  |  | Hydrogen Peroxide |  |  | Liquid Ton | 790 | 790 | 790 | 790 | Liquid Gal | 3.739 | 3.739 | 3.739 | 3.739 | Dry Ton | 2257.1429 | 2257.1429 | 2257.1429 | 2257.1429
Potassium Permanganate | 6.8397 |  | 43637.2397 |  | 13679.3855 |  | Dry Lb | 4.1453 |  | Bin | 5 |  | 52635 |  |  | Potassium Permanganate |  |  | Dry Lb | 3.19 | 3.19 | 3.19 | 3.19 | Liquid Gal | 0.82128 | 0.82128 | 0.82128 | 0.82128 | Dry Ton | 6380 | 6380 | 6380 | 6380
Sodium Hydroxide | 770.3645 |  | 708735.3337 |  | 3081457.9726 |  | Liquid Lb | 68.4768 |  | Truck Ld | 69 |  | 714150 |  |  | Sodium Hydroxide |  |  | Liquid Lb | 0.24 | 0.24 | 0.24 | 0.23 | Liquid Gal | 3.0825 | 3.0825 | 3.0825 | 2.954 | Dry Ton | 960 | 960 | 960 | 920
Note on AD6: jamoore: Feed to AR FIC.
Note on AD14: jamoore: Feed to AR FIC.
Note on U20: jamoore: Enter quarterly pricing chnages into this section.
Note on E21: jamoore: Based on the latest quarter pricing available.
Note on L22: jamoore: 27,000lb Load
Note on V22: Conte, Chris: Pricing changed to Liquid Lb in 2016 from Liquid Gal.
Note on L23: jamoore: 400 gallon transfer from tote.
Note on AA23: jamoore: Pricing per gallon @ 0.50% strength. Neat liquid cost is $12.138 per gallon or $1.40 per pound.
Note on AB23: jamoore: Neat liquid cost is $12.138 per gallon or $1.40 per pound.
Note on AC23: jamoore: Neat liquid cost is $12.138 per gallon or $1.40 per pound.
Note on AD23: jamoore: Neat liquid cost is $12.138 per gallon or $1.40 per pound.
Note on L24: jamoore: 40,000lb Load
Note on L25: jamoore: 45,000lb Load
Note on AA25: jamoore: Pricing per gallon @ 5.50% strength.
Note on AB25: jamoore: Pricing per gallon @ 5.50% strength.
Note on AC25: jamoore: Pricing per gallon @ 5.50% strength.
Note on AD25: jamoore: Pricing per gallon @ 5.50% strength.
Note on L26: jamoore: 45,000lb Load
Note on L27: jamoore: 8 Ton Load
Note on L28: jamoore: 45,000lb Load
Note on V28: Conte, Chris: 2019 1st quarter pricing per P.O. 19P0032.
Note on L29: jamoore: 45,000lb Load
Note on L30: jamoore: 3300lb Bin
Note on AA30: jamoore: Pricing per gallon @ 3.0% strength.
Note on AB30: jamoore: Pricing per gallon @ 3.0% strength.
Note on AC30: jamoore: Pricing per gallon @ 3.0% strength.
Note on AD30: jamoore: Pricing per gallon @ 3.0% strength.
Note on L31: jamoore: 45,000lb Load

## JANUARY
Current Application Point |  | Notes: Chemical are arranged in general process flow
Not in Use
| South Platte | [6 empty] | Aurora Reservoir | [5 empty] | Filters/Adsorbers | [5 empty] | Finished Water | [6 empty] | From Chlorinator 5 | Valve Vault 1 (To Wemlinger RWAR) | RWAR Flow to Process | RWSP Flow to Process | Finished Water Flow | AR Net to Distribution | SP Net to Distribution | AR to Total Flow Blend | Blended&RW | Softening | Pre-Chem | Floc/Sed | UV/AOP | Filtration/Ad | Post-Chem | Finished | Recycle | Control
[45 empty] | pass | bwpfyearly
| KMnO4 (RW) | FeCl3 (Rapid Mix & Flow Split) | NaOH (Rapid Mix) | PEC/PEA (Reactors) | PEA (Sludge) | CO2 (Post Softening) | H202 (UV) | KMnO4 (RW) | FeCl3 (Rapid Mix) | PEC (Rapid Mix) | PAC (Basin 1 & 2) | PEA (Basin 1 & 2) | PEA (Sludge) | PEN AR (FIC) | PEN SP (FIC) | PEN AR (Individual Filters) | PEN SP (Individual Filters) | FeCl3 AR (Backwash Supply) | FeCl3 SP (Backwash Supply) | Cl2 AR | Cl2 SP | NH3 AR (CCB Effluent) | NH3 SP (CCB Effluent) | NaOH AR (CCB Effluent) | NaOH SP (CCB Effluent) | Fluoride(CCB Effluent) | Cl2 to RWAR, RWSP, ARFIC, or SPFIC | KMnO4 (RWAR to Wemlinger) |  |  | Total Produced From Binney
| Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Gallons per Day | MGD | MGD | MGD | MGD | MGD | Ratio | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day
2019-01-01 |  | 75.598 | 829.9988 | 21.1594 | 0 | 1693.9287 | 26.6944 | 118.868 | 339.361 | 18.4026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211.4192 | 158.5397 | 29.9693 | 22.4734 | 62.8465 | 47.1275 | 0 | 58.7258 | 0 | 8.3508 | 6.1013 | 14.0061 | 7.9341 | 5.9496 | 0.57147 | 400.4759 | 1420.2072 | 2834.6983 | 520.5252 | 3906.6801 | 2673.1881 | 848.7102 | 1956.5249 | 502.4581 | 517.457
2019-01-02 |  | 75.4555 | 815.0102 | 21.2004 | 0 | 1679.1635 | 26.7318 | 117.6828 | 336.0752 | 18.1873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217.8687 | 163.375 | 29.6441 | 22.2295 | 63.698 | 47.7657 | 0 | 58.4011 | 0 | 8.2703 | 6.0966 | 14.1298 | 8.0003 | 5.9993 | 0.57147 | 369.7261 | 1368.8998 | 2782.1455 | 521.4564 | 3906.6801 | 2688.3537 | 792.1237 | 1940.3369 | 466.0023 | 645.757
2019-01-03 |  | 75.34 | 813.2062 | 24.288 | 0 | 1600.711 | 26.7347 | 117.9116 | 336.5209 | 18.2718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.3115 | 154.0259 | 28.9503 | 20.8066 | 63.4497 | 45.6013 | 0 | 58.4089 | 0 | 8.2802 | 6.0964 | 13.5435 | 7.8072 | 5.611 | 0.58183 | 338.5374 | 1339.033 | 2792.7928 | 521.4564 | 3906.6801 | 2629.8951 | 729.3308 | 1951.3578 | 430.6215 | 609.1464
2019-01-04 |  | 75.1264 | 814.5928 | 28.9925 | 0 | 1589.8181 | 26.7899 | 117.0838 | 341.0493 | 18.5423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.7029 | 159.9297 | 30.9769 | 23.0743 | 64.8733 | 48.3234 | 0 | 59.0434 | 0 | 8.3912 | 6.1048 | 13.7344 | 7.7866 | 5.8001 | 0.5731 | 313.7415 | 1294.8662 | 2792.3769 | 521.4564 | 3906.6801 | 2620.0783 | 692.3931 | 1958.1464 | 399.6528 | 567.6796
2019-01-05 |  | 75.3299 | 814.9819 | 30.3364 | 0 | 1631.1995 | 26.8023 | 114.0111 | 341.0246 | 18.7438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212.8553 | 155.88 | 31.2489 | 22.8845 | 64.8272 | 47.4748 | 0 | 59.3532 | 0 | 8.3914 | 6.1083 | 13.7307 | 7.8006 | 5.7126 | 0.57726 | 304.9465 | 1287.2733 | 2837.3825 | 521.4564 | 3906.6801 | 2497.4604 | 626.374 | 1919.0027 | 388.2147 | 605.2996
2019-01-06 |  | 75.2604 | 820.4401 | 30.3934 | 0 | 1610.8315 | 26.8755 | 113.4512 | 339.1711 | 18.2632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.038 | 162.0002 | 31.7263 | 23.7905 | 65.0773 | 48.7995 | 0 | 59.7202 | 0 | 8.3462 | 6.124 | 14.0994 | 7.9323 | 5.9482 | 0.57147 | 306.7909 | 1290.4738 | 2782.4701 | 521.4564 | 3906.6801 | 2502.6736 | 587.9542 | 1911.7064 | 390.1587 | 594.5309
2019-01-07 |  | 75.8546 | 829.4996 | 30.3729 | 0 | 1664.2679 | 27.0282 | 113.5508 | 343.0041 | 18.6315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212.6454 | 159.2333 | 31.0566 | 23.2559 | 64.7353 | 48.4751 | 0 | 59.9287 | 0 | 8.4386 | 6.1619 | 13.8884 | 7.8093 | 5.8477 | 0.57181 | 327.1516 | 1316.396 | 2808.4392 | 521.4564 | 3906.6801 | 2583.0776 | 612.9568 | 1950.896 | 406.2694 | 649.1149
2019-01-08 |  | 75.6414 | 813.3225 | 30.1977 | 0 | 1685.5631 | 26.7898 | 108.314 | 339.5791 | 18.5112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.9439 | 161.262 | 31.8386 | 23.887 | 65.0329 | 48.791 | 0 | 59.7164 | 0 | 8.3567 | 6.1054 | 14.2132 | 7.9985 | 6.0009 | 0.57135 | 335.6591 | 1331.3942 | 2812.2346 | 521.4564 | 3906.6801 | 2560.3616 | 630.8034 | 1960.1996 | 415.3459 | 641.3569
2019-01-09 |  | 74.9271 | 806.8892 | 30.1236 | 0 | 1645.4698 | 26.6882 | 108.2548 | 339.9597 | 18.566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.7744 | 157.3345 | 31.1383 | 23.3543 | 64.4524 | 48.3404 | 0 | 59.7193 | 0 | 8.3659 | 6.1137 | 14.0734 | 7.9237 | 5.9429 | 0.57142 | 327.6443 | 1315.7351 | 2826.0259 | 521.4564 | 3906.6801 | 2609.6395 | 626.7815 | 1953.0369 | 416.0204 | 645.2458
2019-01-10 |  | 75.2185 | 812.8723 | 29.9399 | 0 | 1925.1152 | 26.7218 | 109.33 | 343.0134 | 18.7234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203.8347 | 152.4546 | 29.7673 | 22.2639 | 63.4193 | 47.4333 | 0 | 59.8004 | 0 | 8.4355 | 6.0914 | 13.7099 | 7.7299 | 5.7814 | 0.5721 | 307.583 | 1287.4127 | 2831.6552 | 521.4564 | 3906.6801 | 2663.0868 | 595.1174 | 1951.497 | 390.6898 | 685.0186
2019-01-11 |  | 75.1998 | 814.6458 | 29.7889 | 0 | 2180.786 | 26.8439 | 106.5197 | 335.1419 | 18.1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211.4948 | 155.974 | 32.1544 | 23.7134 | 64.6153 | 47.6527 | 0 | 58.5102 | 0 | 8.261 | 6.128 | 14.2069 | 7.8964 | 5.8234 | 0.57554 | 329.0918 | 1312.539 | 2835.77 | 457.1466 | 3141.7263 | 2853.2294 | 627.0571 | 1996.167 | 417.6427 | 660.5347
2019-01-12 |  | 75.2801 | 811.7067 | 29.6915 | 0 | 2230.2666 | 26.6761 | 107.1483 | 336.4518 | 18.2628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.8773 | 156.6706 | 31.8269 | 23.8721 | 63.6731 | 47.7587 | 0 | 59.7203 | 0 | 8.2793 | 6.0829 | 13.9373 | 7.8874 | 5.916 | 0.57141 | 339.3544 | 1334.0431 | 2823.7328 | 185.5865 | 1122.6849 | 2566.7383 | 649.5306 | 1940.9743 | 426.9601 | 564.8879
2019-01-13 |  | 74.2199 | 807.5705 | 29.5808 | 0 | 2127.5226 | 26.6987 | 107.8583 | 339.4626 | 18.4087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.9141 | 156.6182 | 30.9344 | 23.1908 | 62.711 | 47.013 | 0 | 59.6475 | 0 | 8.3639 | 6.0801 | 13.9268 | 7.8595 | 5.8921 | 0.57153 | 339.1902 | 1327.0641 | 2801.286 | 442.2671 | 1126.8936 | 2520.5181 | 647.6497 | 1959.3438 | 426.016 | 580.5813
2019-01-14 |  | 74.7757 | 830.4641 | 30.0266 | 0 | 2227.5352 | 26.6778 | 106.6521 | 335.0539 | 18.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.2834 | 162.0708 | 32.488 | 24.3447 | 64.828 | 48.5785 | 0 | 58.5204 | 0 | 8.245 | 6.0787 | 14.1607 | 7.9992 | 5.9942 | 0.57164 | 337.4444 | 1333.1764 | 2826.8446 | 209.2688 | 1157.3207 | 2668.0633 | 647.3478 | 1936.7361 | 427.6779 | 610.2924
2019-01-15 |  | 75.0856 | 843.1323 | 30.0172 | 0 | 2429.9051 | 26.6581 | 106.9821 | 335.981 | 18.3496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.4218 | 160.8171 | 32.2844 | 24.2134 | 64.4853 | 48.3642 | 0 | 59.0687 | 0 | 8.2673 | 6.0774 | 14.1232 | 8.0001 | 6.0001 | 0.57143 | 337.6675 | 1342.0635 | 2865.7721 | 209.2688 | 1157.3207 | 2675.77 | 640.5942 | 1950.2357 | 418.6077 | 622.6788
2019-01-16 |  | 75.002 | 829.1832 | 29.8109 | 0 | 2461.2893 | 26.7068 | 108.173 | 339.8408 | 18.4945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207.5863 | 155.2446 | 31.0642 | 23.2316 | 62.5126 | 46.7504 | 0 | 59.2699 | 0 | 8.3591 | 6.0867 | 13.669 | 7.747 | 5.7936 | 0.57213 | 318.4126 | 1313.5521 | 3126.0988 | 209.2688 | 1157.3207 | 2661.7883 | 616.5619 | 1958.0365 | 395.7365 | 619.432
2019-01-17 |  | 74.7524 | 826.4126 | 30.0322 | 0 | 2419.4918 | 26.6112 | 107.1372 | 336.4826 | 18.3126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206.8824 | 151.1751 | 31.0869 | 22.7161 | 61.9512 | 45.2696 | 0 | 59.075 | 0 | 8.2797 | 6.0737 | 13.4404 | 7.6902 | 5.6194 | 0.57779 | 317.2417 | 1313.7087 | 2853.9617 | 209.2688 | 1157.3207 | 2609.6709 | 609.0814 | 1948.2741 | 390.7405 | 596.3477
2019-01-18 |  | 74.6749 | 826.8866 | 29.9675 | 0 | 2349.9052 | 26.7223 | 107.1457 | 336.4183 | 18.2251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213.2104 | 159.8774 | 32.5199 | 24.3853 | 64.6966 | 48.5133 | 0 | 59.0752 | 0 | 8.2773 | 6.0783 | 14.133 | 8.0009 | 5.9995 | 0.57148 | 337.2999 | 1344.0672 | 2879.1132 | 209.2688 | 1157.3207 | 2661.9004 | 625.2847 | 1930.3774 | 413.8441 | 579.6156
2019-01-19 |  | 74.5866 | 826.6918 | 29.9505 | 0 | 2329.3523 | 26.7462 | 107.1668 | 336.5435 | 18.4331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207.2663 | 155.4468 | 31.1414 | 23.3556 | 63.6241 | 47.7172 | 0 | 59.0734 | 0 | 8.2809 | 6.0751 | 13.8389 | 7.8298 | 5.8722 | 0.57143 | 342.8476 | 1339.3744 | 2835.605 | 209.2688 | 1157.3207 | 2643.755 | 644.6139 | 1969.2553 | 414.3839 | 546.0672
2019-01-20 |  | 74.5009 | 829.2449 | 29.9946 | 0 | 2290.0949 | 26.7933 | 107.7853 | 338.5713 | 18.5035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.8878 | 157.1774 | 31.2737 | 23.4198 | 64.545 | 48.3354 | 0 | 59.694 | 0 | 8.3314 | 6.0757 | 14.0097 | 7.9396 | 5.9457 | 0.5718 | 318.4894 | 1303.5548 | 2828.6746 | 209.2688 | 1157.3207 | 2562.6598 | 611.8924 | 1943.7301 | 389.956 | 538.6064
2019-01-21 |  | 74.5996 | 834.6942 | 30.0047 | 0 | 2323.3495 | 26.6512 | 107.1588 | 336.3575 | 18.2522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211.697 | 158.7436 | 31.4018 | 23.547 | 65.0801 | 48.8011 | 0 | 59.7269 | 0 | 8.2765 | 6.0766 | 14.1195 | 8.0015 | 6.0001 | 0.57147 | 314.1253 | 1294.8974 | 2885.734 | 209.2688 | 1157.3207 | 2525.2429 | 590.3055 | 1930.5473 | 391.9569 | 544.6401
2019-01-22 |  | 75.5321 | 831.6633 | 29.7015 | 0 | 2379.7073 | 26.6798 | 106.9416 | 336.0719 | 18.2618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207.607 | 155.6723 | 31.216 | 23.4071 | 63.7864 | 47.8297 | 0 | 59.7142 | 0 | 8.2707 | 6.0819 | 13.8286 | 7.831 | 5.872 | 0.57148 | 364.5559 | 1365.3684 | 2874.8968 | 209.2688 | 1157.3207 | 2699.449 | 662.7345 | 1941.8538 | 456.2644 | 614.8509
2019-01-23 |  | 75.1579 | 802.9968 | 29.8285 | 0 | 2264.2223 | 26.6511 | 110.9864 | 341.0846 | 18.5417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206.8072 | 151.1792 | 30.9119 | 22.5971 | 63.1184 | 46.1405 | 0 | 59.2907 | 0 | 8.391 | 6.0786 | 13.557 | 7.7105 | 5.6365 | 0.5777 | 369.3566 | 1360.8784 | 2985.382 | 209.2688 | 1157.3207 | 2698.5226 | 680.3395 | 1961.3778 | 430.8844 | 624.4012
2019-01-24 |  | 68.5673 | 735.5228 | 27.2446 | 0 | 1690.9826 | 24.5274 | 124.6273 | 398.5078 | 21.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249.3731 | 123.2687 | 38.3302 | 18.9471 | 84.1369 | 41.5901 | 0 | 63.3177 | 0 | 9.8003 | 5.5619 | 14.0036 | 9.2435 | 4.5692 | 0.6692 | 364.1286 | 1357.3446 | 2825.0254 | 209.2688 | 1157.3207 | 2666.2849 | 682.5054 | 1930.5099 | 409.3787 | 645.6891
2019-01-25 |  | 75.0638 | 786.5499 | 29.7333 | 0 | 1650.3887 | 26.6413 | 110.9492 | 339.9427 | 18.5732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213.4617 | 160.0595 | 30.0408 | 22.5254 | 68.63 | 51.4607 | 0 | 59.7087 | 0 | 8.3645 | 6.0682 | 13.9217 | 7.8314 | 5.8722 | 0.57148 | 359.3305 | 1359.2177 | 3604.7924 | 209.2688 | 1157.3207 | 2705.8474 | 675.1793 | 1946.7099 | 446.3174 | 645.3137
2019-01-26 |  | 74.9098 | 786.1788 | 29.7627 | 0 | 1710.0546 | 26.6232 | 111.6501 | 341.8334 | 18.6695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.2391 | 170.2408 | 31.6237 | 23.6916 | 68.3433 | 51.2008 | 0 | 59.3422 | 0 | 8.4115 | 6.0699 | 14.0725 | 7.9345 | 5.9443 | 0.5717 | 350.0643 | 1355.4308 | 3076.4017 | 209.2688 | 1157.3207 | 2618.6412 | 650.2884 | 1947.7377 | 440.8353 | 589.4427
2019-01-27 |  | 74.7897 | 786.1637 | 29.8232 | 0 | 1755.7256 | 26.5684 | 111.0294 | 339.6372 | 18.3596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233.2255 | 174.9359 | 32.5431 | 24.4096 | 68.9784 | 51.7387 | 0 | 58.5429 | 0 | 8.3577 | 6.0698 | 14.2159 | 7.9994 | 6.0002 | 0.57141 | 332.2463 | 1327.8618 | 2917.9599 | 209.2688 | 1157.3207 | 2621.0088 | 630.8059 | 1950.1253 | 416.5785 | 584.2962
2019-01-28 |  | 74.8506 | 786.3029 | 29.745 | 0 | 1817.285 | 26.5698 | 110.9446 | 339.9266 | 18.2864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213.4425 | 160.0567 | 31.6472 | 23.7316 | 64.5431 | 48.3997 | 0 | 58.8813 | 0 | 8.3648 | 6.0711 | 13.7948 | 7.7587 | 5.8181 | 0.57147 | 347.2613 | 1352.6864 | 2880.3697 | 209.2688 | 1157.3207 | 2744.306 | 649.7036 | 1944.4966 | 448.0553 | 620.3422
2019-01-29 |  | 74.6318 | 763.776 | 29.7151 | 0 | 1851.5033 | 26.6765 | 110.9284 | 340.1472 | 18.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218.3796 | 153.4379 | 29.1855 | 20.5063 | 64.6475 | 45.4226 | 0 | 59.375 | 0 | 8.3661 | 6.07 | 13.4076 | 7.7736 | 5.4619 | 0.58733 | 358.6646 | 1368.7232 | 2990.7391 | 209.2688 | 1157.3207 | 2713.1375 | 679.156 | 1938.827 | 459.8223 | 664.6472
2019-01-30 |  | 74.6517 | 762.0207 | 29.7281 | 0 | 1868.3233 | 26.6425 | 109.8719 | 336.466 | 18.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.8134 | 170.8709 | 30.8648 | 23.1501 | 68.7081 | 51.5343 | 0 | 59.0678 | 0 | 8.2793 | 6.0673 | 14.1297 | 8.0001 | 6.0004 | 0.57141 | 341.8906 | 1350.7284 | 2900.3414 | 209.2688 | 1157.3207 | 2691.2719 | 658.4114 | 1961.4104 | 441.9269 | 640.8237
2019-01-31 |  | 74.4059 | 761.8307 | 29.7836 | 0 | 1810.1894 | 26.5524 | 109.846 | 336.3119 | 18.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.8539 | 164.8676 | 31.3213 | 23.4877 | 66.8507 | 50.1311 | 0 | 64.5395 | 0 | 8.2763 | 6.066 | 14.0085 | 7.9326 | 5.9487 | 0.57146 | 329.0934 | 1329.1656 | 2930.8651 | 209.2688 | 1157.3207 | 2656.4867 | 619.5227 | 1958.2721 | 423.0966 | 611.941
Monthly Chemical/Power Usage | 0 | 2318.9901 | 25054.4517 | 900.9351 | 0 | 60893.9488 | 825.7742 | 3435.9604 | 10554.9931 | 573.6992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6662.1189 | 4898.44 | 972.1772 | 714.4634 | 2026.8769 | 1488.3344 | 0 | 1845.9791 | 0 | Total MG | Total MG | Total MG | Total MG | Total MG | Overall Ratio | 10480.0131 | 41337.1374 | 89649.5874 | 10065.4716 | 65289.8776 | 81792.107 | 20241.1111 | 60397.7029 | 13092.1157 | 18866.0387
Cost per Gallon or lb or kW*Hr | 0.82128 | 1.4864 | 3.0825 | 3.9899 | 0 | 0.05795 | 3.739 | 0.82128 | 1.4864 | 3.9899 | 0 | 0 | 0 | 15.77 | 15.77 | 15.77 | 15.77 | 1.4864 | 1.4864 | 0.2996 | 0.2996 | 0.74349 | 0.74349 | 3.0825 | 3.0825 | 0 | 0.2996 | 0.82128 | 259.7306 | 188.2218 | 431.6341 | 245.5894 | 180.5737 | 0.57628 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067
Cost Per Month | 0 | 3446.8421 | 77229.4455 | 3594.6014 | 0 | 3528.8043 | 3087.5951 | 2821.8993 | 15688.4646 | 2288.9774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1995.9708 | 1467.5726 | 722.8082 | 531.1995 | 6247.775 | 4587.7372 | 0 | 553.0553 | 0 | [6 empty] | 702.1609 | 2769.5882 | 6006.5224 | 674.3866 | 4374.4218 | 5480.0712 | 1356.1544 | 4046.6461 | 877.1718 | 1264.0246
2019-01-01 | [33 empty] | Natural Gas | 1677.99 | NA | 3039.05 | 1197.68 | 1687.32 | 8722.17 | 1961.15 | NA | 288.84 | 650.95
Total Binney WPF Costs |  |  | South Platte Costs |  |  | Aurora Reservoir Costs |  |  | Labor Costs | [7 empty] | Monthly Truck Loads
Chemical | 127792.7483 |  | Chemical | 97473.7977 |  | Chemical | 29765.8953 |  | Monthly | 105629.83 | [6 empty] | Chemical |  | Gallon/Lbs | Loads
Electrical | 27551.1479 |  | Electrical | 16126.6758 |  | Electrical | 11424.4721 | [9 empty] | Ammonia |  | 1686.6406 | 0.46628
Natural Gas | 19225.15 |  | Natural Gas | 8914.4705 |  | Natural Gas | 10310.6795 |  | Material Costs | [7 empty] | Anionic Polymer |  | 0 | 0
Labor | 105629.83 |  | Labor | 52814.915 |  | Labor | 52814.915 |  | Monthly | 24518.36 | [6 empty] | Carbon Dioxide |  | 60893.9488 | 1.5223
Materials | 24518.36 |  | Materials | 12259.18 |  | Materials | 12259.18 | [9 empty] | Carbon PAC |  | 0 | 0
Binney MG Produced | 431.6341 |  | Net South Platte MG Produced | 180.5737 |  | Net Aurora Reservoir MG Produced | 245.5894 | [9 empty] | Cationic Polymer |  | 1474.6344 | 0.28423
Total Treated (MG) | 447.9524 |  | RWSP to Process (MG) | 188.2218 |  | RWAR to Process (MG) | 259.7306
Binney Cost per MG | 680.2447 |  | South Platte Cost per MG | 996.6382 |  | Aurora Reservoir Cost per MG | 448.831 | [9 empty] | Chlorine |  | 13406.5379 | 0.83791
Binney Cost per KG | 0.68024 |  | South Platte Cost per KG | 0.99664 | 539.8006 | Aurora Reservoir Cost per KG | 0.44883 | 121.2019 | [8 empty] | Ferric Chloride |  | 12873.9832 | 3.3404
[17 empty] | Hydrogen Peroxide |  | 825.7742 | 0.1737
Notes: | [16 empty] | Potassium Permanganate |  | 3435.9604 | 0.26806
1. The difference between the "Binney MG Produced" and the Net numbers is the ammont of water needed from distribution to create the finished water (W3 to Chlorine and NaOH Motive) | [16 empty] | Sodium Hydroxide |  | 28569.663 | 8.1542
Note on B40: Peter Bong: 3% Solution Strength
Note on C40: Peter Bong: 40% Solution Strength
Note on D40: Peter Bong: 50% Solution Strength
Note on E40: Peter Bong: 100% Solution Strength, PEC Cost
Note on F40: Peter Bong: 0.5% Solution Strength
Note on G40: Peter Bong: 99% Solution Strength
Note on H40: Peter Bong: 35% Solution Strength
Note on I40: Peter Bong: 3% Solution Strength
Note on J40: Peter Bong: 40% Solution Strength
Note on K40: Peter Bong: 100% Solution Strength
Note on L40: Peter Bong: 5.5% Solution Strength
Note on M40: Peter Bong: 0.5% Solution Strength
Note on N40: Peter Bong: 0.5% Solution Strength
Note on O40: Peter Bong: 100% Solution Strength
Note on P40: Peter Bong: 100% Solution Strength
Note on Q40: Peter Bong: 100% Solution Strength
Note on R40: Peter Bong: 100% Solution Strength
Note on S40: Peter Bong: 40% Solution Strength
Note on T40: Peter Bong: 40% Solution Strength
Note on U40: Peter Bong: 100% Solution Strength
Note on V40: Peter Bong: 100% Solution Strength
Note on Y40: Peter Bong: 50% Solution Strength
Note on Z40: Peter Bong: 50% Solution Strength
Note on AB40: Peter Bong: 100% Solution Strength
Note on AC40: Peter Bong: 3% Solution Strength
Note on AJ40: Peter Bong: Cost per kW*Hr
Note on AK40: Peter Bong: Cost per kW*Hr
Note on AL40: Peter Bong: Cost per kW*Hr
Note on AM40: Peter Bong: Cost per kW*Hr
Note on AN40: Peter Bong: Cost per kW*Hr
Note on AO40: Peter Bong: Cost per kW*Hr
Note on AP40: Peter Bong: Cost per kW*Hr
Note on AQ40: Peter Bong: Cost per kW*Hr
Note on AR40: Peter Bong: Cost per kW*Hr
Note on AS40: Peter Bong: Cost per kW*Hr
Note on AI42: Peter Bong: See Utility Summary Seet For Data

## FEBRUARY
Current Application Point |  | Notes: Chemical are arranged in general process flow
Not in Use
| South Platte | [6 empty] | Aurora Reservoir | [5 empty] | Filters/Adsorbers | [5 empty] | Finished Water | [6 empty] | From Chlorinator 5 | Valve Vault 1 (To Wemlinger RWAR) | RWAR Flow to Process | RWSP Flow to Process | Finished Water Flow | AR Net to Distribution | SP Net to Distribution | AR to Total Flow Blend | Blended&RW | Softening | Pre-Chem | Floc/Sed | UV/AOP | Filtration/Ad | Post-Chem | Finished | Recycle | Control
[45 empty] | pass | bwpfyearly
| KMnO4 (RW) | FeCl3 (Rapid Mix & Flow Split) | NaOH (Rapid Mix) | PEC/PEA (Reactors) | PEA (Sludge) | CO2 (Post Softening) | H202 (UV) | KMnO4 (RW) | FeCl3 (Rapid Mix) | PEC (Rapid Mix) | PAC (Basin 1 & 2) | PEA (Basin 1 & 2) | PEA (Sludge) | PEN AR (FIC) | PEN SP (FIC) | PEN AR (Individual Filters) | PEN SP (Individual Filters) | FeCl3 AR (Backwash Supply) | FeCl3 SP (Backwash Supply) | Cl2 AR | Cl2 SP | NH3 AR (CCB Effluent) | NH3 SP (CCB Effluent) | NaOH AR (CCB Effluent) | NaOH SP (CCB Effluent) | Fluoride(CCB Effluent) | Cl2 to RWAR, RWSP, ARFIC, or SPFIC | KMnO4 (RWAR to Wemlinger) |  |  | Total Produced From Binney
| Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Gallons per Day | MGD | MGD | MGD | MGD | MGD | Ratio | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day
2019-02-01 |  | 71.2147 | 756.1209 | 29.9465 | 0 | 1781.9931 | 26.4703 | 110.8201 | 339.4272 | 18.3237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212.0842 | 158.9751 | 30.5212 | 22.8782 | 62.3611 | 46.745 | 0 | 68.3286 | 0 | 8.3527 | 6.0724 | 13.6392 | 7.7126 | 5.7813 | 0.57156 | 310.6228 | 1296.7137 | 2932.155 | 209.2688 | 1157.3207 | 2619.5337 | 608.6053 | 1974.2918 | 409.8734 | 600.2182
2019-02-02 |  | 69.6142 | 748.3835 | 30.1365 | 0 | 1744.4912 | 26.429 | 109.5432 | 335.4074 | 18.207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212.7836 | 153.9339 | 30.6728 | 22.1896 | 63.1271 | 45.668 | 0 | 68.4293 | 0 | 8.2537 | 6.0596 | 13.6534 | 7.8514 | 5.6799 | 0.58024 | 295.7621 | 1275.7757 | 2908.1628 | 338.24 | 1157.3207 | 2555.492 | 610.7028 | 1931.0775 | 395.26 | 590.8823
2019-02-03 |  | 69.4652 | 753.6676 | 30.1753 | 0 | 1741.6448 | 26.6208 | 109.6164 | 335.7624 | 18.0795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212.7168 | 159.5548 | 30.5346 | 22.9034 | 63.936 | 47.9572 | 0 | 68.1409 | 0 | 8.2627 | 6.0641 | 14.0029 | 7.9343 | 5.9514 | 0.5714 | 287.8369 | 1278.0539 | 2889.3947 | 451.0898 | 1157.3207 | 2488.8559 | 594.2096 | 1910.4635 | 388.8388 | 621.6849
2019-02-04 |  | 69.2343 | 753.3903 | 30.1755 | 0 | 1743.8857 | 26.5846 | 110.8584 | 339.8046 | 18.5949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.8242 | 157.1019 | 30.4294 | 22.7834 | 63.3296 | 47.4168 | 0 | 68.5803 | 0 | 8.3579 | 6.0618 | 13.8425 | 7.8231 | 5.8574 | 0.57184 | 296.7086 | 1296.8781 | 2907.1659 | 451.0898 | 1157.3207 | 2493.041 | 605.6664 | 1924.1517 | 395.9882 | 627.0126
2019-02-05 |  | 66.4965 | 753.4015 | 30.1112 | 0 | 1707.5453 | 26.474 | 109.8181 | 336.2045 | 18.4124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.7265 | 147.2623 | 30.7398 | 21.5844 | 63.0573 | 44.2765 | 0 | 68.9989 | 0 | 8.2738 | 6.0618 | 13.4495 | 7.8203 | 5.4912 | 0.58749 | 304.5086 | 1301.2428 | 3271.5661 | 451.0898 | 1157.3207 | 2541.5942 | 629.7234 | 1921.0958 | 424.4418 | 601.3388
2019-02-06 |  | 61.169 | 749.4916 | 30.012 | 0 | 1694.5792 | 26.6217 | 109.758 | 336.3696 | 18.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.4721 | 160.8909 | 32.349 | 24.2673 | 64.553 | 48.4259 | 0 | 68.9964 | 0 | 8.2771 | 6.0601 | 14.1352 | 7.9994 | 6.0009 | 0.57137 | 323.4885 | 1323.2928 | 2848.597 | 451.0898 | 1157.3207 | 2633.1554 | 687.4289 | 1931.929 | 490.7275 | 624.5988
2019-02-07 |  | 59.2896 | 744.9964 | 28.0033 | 0 | 1881.4448 | 26.5483 | 110.547 | 338.707 | 18.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.9336 | 144.4884 | 29.5705 | 21.3701 | 61.9846 | 44.7951 | 0 | 69.2054 | 0 | 8.3342 | 6.0576 | 13.3578 | 7.6601 | 5.5358 | 0.58049 | 339.5477 | 1341.2006 | 2842.0926 | 451.0898 | 1157.3207 | 2690.5673 | 739.8123 | 1953.4589 | 505.7721 | 646.7752
2019-02-08 |  | 58.5504 | 744.9916 | 26.5704 | 0 | 1898.6705 | 26.5424 | 109.9459 | 336.7713 | 18.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211.8557 | 158.8824 | 30.4734 | 22.8537 | 63.8624 | 47.894 | 0 | 70.3396 | 0 | 8.2846 | 6.0586 | 13.9746 | 7.9199 | 5.9396 | 0.57144 | 330.8866 | 1319.7996 | 2942.9793 | 451.0898 | 1157.3207 | 2628.8287 | 703.9044 | 1943.5512 | 495.195 | 634.1364
2019-02-09 |  | 57.9434 | 744.8204 | 26.636 | 0 | 1888.8942 | 26.5629 | 109.9548 | 336.8379 | 18.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.8109 | 161.0994 | 30.7919 | 23.0927 | 63.8452 | 47.8813 | 0 | 70.9722 | 0 | 8.2885 | 6.0569 | 13.9673 | 7.9035 | 5.9273 | 0.57144 | 322.5749 | 1294.1681 | 2838.9542 | 451.0898 | 1157.3207 | 2571.6708 | 680.7634 | 1945.7382 | 470.519 | 595.2303
2019-02-10 |  | 58.525 | 745.9272 | 27.1134 | 0 | 1938.2553 | 26.6606 | 109.8542 | 336.482 | 18.1524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207.0195 | 136.5975 | 29.8321 | 19.6841 | 65.6586 | 43.3235 | 0 | 71.4876 | 0 | 8.2795 | 6.0661 | 12.7773 | 7.6097 | 5.0211 | 0.60247 | 318.5115 | 1305.6809 | 2854.1774 | 451.0898 | 1157.3207 | 2569.5196 | 664.1636 | 1920.886 | 448.0021 | 573.1066
2019-02-11 |  | 57.8484 | 736.7702 | 26.7546 | 0 | 1879.9237 | 26.547 | 110.2735 | 340.2363 | 18.3061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217.1603 | 162.1178 | 30.8366 | 23.0206 | 66.8696 | 49.9206 | 0 | 71.608 | 0 | 8.3956 | 6.0565 | 14.2802 | 7.9113 | 5.9061 | 0.57256 | 321.8946 | 1255.6821 | 2704.4819 | 391.7856 | 1168.5934 | 2460.4437 | 654.8778 | 1939.0746 | 446.5427 | 613.6831
2019-02-12 |  | 59.4268 | 744.6938 | 26.8786 | 0 | 1910.1014 | 26.4855 | 111.0068 | 340.1416 | 18.4058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.2546 | 160.6968 | 31.8349 | 23.877 | 65.9099 | 49.4342 | 0 | 71.7241 | 0 | 8.3694 | 6.0558 | 14.2438 | 7.9996 | 5.9999 | 0.57142 | 313.9862 | 1289.3817 | 2619.5801 | 496.5045 | 1215.4225 | 2634.1002 | 663.0068 | 1945.0424 | 437.9516 | 633.7138
2019-02-13 |  | 58.6779 | 744.5934 | 26.9345 | 0 | 1932.8304 | 26.5269 | 110.869 | 339.8083 | 18.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.9786 | 157.4775 | 30.6149 | 22.9603 | 64.6941 | 48.5186 | 0 | 71.7292 | 0 | 8.3625 | 6.0549 | 13.9086 | 7.82 | 5.8647 | 0.57144 | 296.2622 | 1264.6092 | 2772.6324 | 496.5045 | 1215.4225 | 2581.9634 | 614.9139 | 1947.8473 | 412.5441 | 659.069
2019-02-14 |  | 59.0992 | 748.4767 | 27.0465 | 0 | 2140.1 | 26.6515 | 110.3499 | 339.6382 | 18.5724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206.6856 | 150.7106 | 30.3611 | 22.1386 | 61.052 | 44.5177 | 0 | 72.0051 | 0 | 8.3548 | 6.0863 | 13.4756 | 7.6737 | 5.5955 | 0.57831 | 300.2558 | 1290.9887 | 2764.9992 | 496.5045 | 1215.4225 | 2514.2235 | 624.1881 | 1922.1234 | 420.8243 | 606.2805
2019-02-15 |  | 58.252 | 744.4466 | 26.6891 | 0 | 1829.8075 | 26.4476 | 105.3322 | 338.8671 | 18.4546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212.219 | 159.1448 | 31.7995 | 23.8467 | 61.1402 | 45.8495 | 0 | 71.7388 | 0 | 8.3384 | 6.054 | 14.2001 | 8.0009 | 6 | 0.57146 | 303.2151 | 1306.1095 | 2773.3638 | 496.5045 | 1215.4225 | 2502.5903 | 637.3619 | 1936.2002 | 427.2746 | 613.3806
2019-02-16 |  | 58.1663 | 744.3384 | 26.685 | 0 | 1769.2234 | 26.4566 | 105.4855 | 339.5924 | 18.4735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.0787 | 157.5654 | 31.6071 | 23.7063 | 60.3698 | 45.2792 | 0 | 71.7335 | 0 | 8.3556 | 6.0529 | 13.9144 | 7.8337 | 5.8755 | 0.57142 | 309.1918 | 1306.5273 | 2841.9548 | 496.5045 | 1215.4225 | 2530.7159 | 642.5032 | 1963.1972 | 450.3024 | 545.6337
2019-02-17 |  | 59.0061 | 745.3656 | 26.645 | 0 | 2019.2434 | 26.6268 | 105.7135 | 340.5975 | 18.5095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.3286 | 156.5838 | 31.9613 | 23.908 | 60.2489 | 45.0679 | 0 | 71.4318 | 0 | 8.3785 | 6.0611 | 13.821 | 7.8032 | 5.837 | 0.57207 | 334.644 | 1336.0049 | 2926.969 | 496.5045 | 1215.4225 | 2565.1564 | 698.2307 | 1959.8691 | 506.575 | 582.8289
2019-02-18 |  | 58.0226 | 756.7678 | 26.8383 | 0 | 2075.7264 | 26.6023 | 106.386 | 342.423 | 18.7915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207.9707 | 150.0723 | 31.0731 | 22.4224 | 59.6653 | 43.0547 | 0 | 72.2034 | 0 | 8.4253 | 6.0392 | 13.5093 | 7.783 | 5.6162 | 0.58085 | 345.8924 | 1331.0413 | 2840.115 | 496.5045 | 1215.4225 | 2590.3745 | 737.2072 | 1949.4534 | 518.7743 | 631.72
2019-02-19 |  | 59.009 | 751.4486 | 26.8262 | 0 | 1950.2783 | 26.4021 | 107.4987 | 345.9327 | 18.7393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.8776 | 156.6651 | 29.9042 | 22.4291 | 62.0389 | 46.5312 | 0 | 73.4204 | 0 | 8.5121 | 6.0459 | 13.9326 | 7.9033 | 5.9278 | 0.57142 | 345.0226 | 1342.0573 | 2898.2202 | 496.5045 | 1215.4225 | 2618.5192 | 755.6376 | 1945.4266 | 517.9747 | 640.1839
2019-02-20 |  | 58.4121 | 752.9023 | 27.1626 | 0 | 2002.2899 | 26.5976 | 107.9402 | 347.4873 | 19.1556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215.3754 | 155.8971 | 28.3192 | 20.4985 | 62.3979 | 45.166 | 0 | 66.646 | 0 | 8.55 | 6.0579 | 13.3694 | 7.6787 | 5.5581 | 0.5801 | 337.4784 | 1324.1679 | 2891.3424 | 496.5045 | 1215.4225 | 2636.1084 | 710.9685 | 1951.8386 | 513.6022 | 625.2811
2019-02-21 |  | 63.7081 | 785.258 | 27.2361 | 0 | 2104.9102 | 26.785 | 107.6988 | 346.6793 | 18.8177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.7762 | 164.3189 | 32.0605 | 22.7295 | 71.6234 | 50.7778 | 0 | 60.1359 | 0 | 8.5308 | 6.112 | 13.6677 | 7.8668 | 5.5772 | 0.58515 | 331.3996 | 1315.6877 | 3123.4024 | 496.5045 | 1215.4225 | 2607.6019 | 684.6716 | 1931.5359 | 515.8787 | 633.7587
2019-02-22 |  | 63.1029 | 835.6839 | 27.396 | 0 | 2325.9422 | 26.6799 | 107.4267 | 346.0559 | 18.8179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4682 | 154.6734 | 31.055 | 22.1898 | 66.6618 | 47.6319 | 0 | 67.3781 | 0 | 8.515 | 6.0762 | 13.5079 | 7.857 | 5.6141 | 0.58325 | 326.105 | 1336.7145 | 3128.1017 | 496.5045 | 1215.4225 | 2590.6179 | 707.5515 | 1930.7963 | 505.7518 | 638.8326
2019-02-23 |  | 55.9251 | 870.8708 | 26.2996 | 0 | 2453.1047 | 26.586 | 107.649 | 345.8962 | 18.8759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213.8061 | 148.8957 | 31.98 | 22.271 | 64.5807 | 44.9744 | 0 | 77.1698 | 0 | 8.5111 | 6.0518 | 13.4021 | 7.8147 | 5.4422 | 0.58948 | 330.1245 | 1336.2337 | 3163.2787 | 496.5045 | 1215.4225 | 2557.8715 | 680.9002 | 1940.372 | 494.8084 | 583.1616
2019-02-24 |  | 53.3466 | 869.1738 | 22.0489 | 0 | 2420.7933 | 26.5532 | 107.7204 | 346.1541 | 18.8849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.7524 | 160.0889 | 31.2284 | 23.0647 | 63.1238 | 46.622 | 0 | 80.731 | 0 | 8.5167 | 6.0402 | 14.0173 | 7.9989 | 5.9078 | 0.57518 | 321.2913 | 1318.4724 | 2857.2674 | 496.5045 | 1215.4225 | 2546.9793 | 674.4914 | 1957.8629 | 489.4932 | 576.1022
2019-02-25 |  | 55.9815 | 900.6882 | 20.7855 | 0 | 2475.3688 | 27.4879 | 117.5921 | 379.0784 | 20.8281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230.8468 | 131.2114 | 33.0323 | 18.7753 | 65.2684 | 37.098 | 0 | 85.0092 | 0 | 9.3264 | 6.2578 | 13.0506 | 8.235 | 4.6807 | 0.6376 | 312.4958 | 1308.2639 | 2851.3112 | 499.4279 | 1215.4225 | 2600.5428 | 664.0844 | 1976.9657 | 494.0344 | 648.6679
2019-02-26 |  | 54.3621 | 877.5199 | 18.7097 | 0 | 2422.3305 | 26.5649 | 107.4769 | 345.9458 | 18.732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.7963 | 151.7932 | 31.0235 | 22.4463 | 60.8023 | 43.9921 | 0 | 79.8472 | 0 | 8.5125 | 6.0499 | 13.3701 | 7.673 | 5.5516 | 0.58021 | 303.5765 | 1285.1793 | 2826.5993 | 527.0549 | 1215.4225 | 2575.0115 | 654.1817 | 1964.2181 | 495.9965 | 653.4332
2019-02-27 |  | 53.6604 | 891.1307 | 17.4315 | 0 | 2478.8431 | 26.6529 | 107.5565 | 346.6675 | 18.9018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211.4022 | 158.5714 | 31.8937 | 23.9232 | 62.212 | 46.6648 | 0 | 79.7389 | 0 | 8.53 | 6.0822 | 13.8754 | 7.8325 | 5.8751 | 0.5714 | 311.9316 | 1306.527 | 2859.4506 | 527.0549 | 1215.4225 | 2589.8052 | 664.9237 | 1973.5828 | 511.7376 | 667.2891
2019-02-28 |  | 53.7978 | 903.567 | 17.087 | 0 | 2529.0043 | 26.779 | 107.988 | 347.905 | 18.8842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207.3605 | 150.074 | 30.6516 | 22.1836 | 61.0659 | 44.1955 | 0 | 81.015 | 0 | 8.5616 | 6.1157 | 13.4001 | 7.7233 | 5.5896 | 0.58014 | 305.9245 | 1308.1642 | 2912.8866 | 527.0549 | 1215.4225 | 2559.7024 | 657.1081 | 1955.0802 | 499.024 | 637.3101
Monthly Chemical/Power Usage | 0 | 1681.307 | 21898.8866 | 734.3348 | 0 | 56741.2257 | 744.9471 | 3052.6796 | 9590.8806 | 521.5634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5955.365 | 4325.3449 | 867.1515 | 629.9979 | 1775.4398 | 1289.6793 | 0 | 2018.7447 | 0 | Total MG | Total MG | Total MG | Total MG | Total MG | Overall Ratio | 8881.1402 | 36594.6188 | 80991.2016 | 13083.1649 | 33403.983 | 72054.5867 | 18651.7886 | 54447.1305 | 13083.7084 | 17305.3139
Cost per Gallon or lb or kW*Hr | 0.82128 | 1.4864 | 3.0825 | 3.9899 | 0 | 0.05795 | 3.739 | 0.82128 | 1.4864 | 3.9899 | 0 | 0 | 0 | 15.77 | 15.77 | 15.77 | 15.77 | 1.4864 | 1.4864 | 0.2996 | 0.2996 | 0.74349 | 0.74349 | 3.0825 | 3.0825 | 0 | 0.2996 | 0.82128 | 236.0111 | 169.9692 | 383.7456 | 219.6428 | 159.6049 | 0.57915 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066
Cost Per Month | 0 | 2499.0188 | 67502.5295 | 2929.8901 | 0 | 3288.154 | 2785.3798 | 2507.1169 | 14255.4514 | 2080.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1784.2273 | 1295.8733 | 644.7222 | 468.3999 | 5472.7292 | 3975.3901 | 0 | 604.8159 | 0 | [6 empty] | 586.1553 | 2415.2448 | 5345.4193 | 863.4889 | 2204.6629 | 4755.6027 | 1231.018 | 3593.5106 | 863.5248 | 1142.1507
2019-02-01 | [33 empty] | Natural Gas | 1446.88 | NA | 3003.44 | 1064.25 | 1762.11 | 8433.42 | 1856.4 | NA | 211.46 | 842.65
bw |  |  | South Platte Costs |  |  | Aurora Reservoir Costs |  |  | Labor Costs | [7 empty] | Monthly Truck Loads
Chemical | 112094.6615 |  | Chemical | 84744.6355 |  | Chemical | 26745.2101 |  | Monthly | 144451.64 | [6 empty] | Chemical |  | Gallon/Lbs | Loads
Electrical | 23000.778 |  | Electrical | 12573.8969 |  | Electrical | 10426.8811 | [9 empty] | Ammonia |  | 1497.1494 | 0.4139
Natural Gas | 18620.61 |  | Natural Gas | 8730.2291 |  | Natural Gas | 9890.3809 |  | Material Costs | [7 empty] | Anionic Polymer |  | 0 | 0
Labor | 144451.64 |  | Labor | 72225.82 |  | Labor | 72225.82 |  | Monthly | 97861.38 | [6 empty] | Carbon Dioxide |  | 56741.2257 | 1.4185
Materials | 97861.38 |  | Materials | 48930.69 |  | Materials | 48930.69 | [9 empty] | Carbon PAC |  | 0 | 0
Binney MG Produced | 383.7456 |  | Net South Platte MG Produced | 159.6049 |  | Net Aurora Reservoir MG Produced | 219.6428 | [9 empty] | Cationic Polymer |  | 1255.8982 | 0.24207
Total Treated (MG) | 405.9803 |  | RWSP to Process (MG) | 169.9692 |  | RWAR to Process (MG) | 236.0111
Binney Cost per MG | 975.4884 |  | South Platte Cost per MG | 1336.7438 |  | Aurora Reservoir Cost per MG | 712.7588 | [9 empty] | Chlorine |  | 12299.4546 | 0.76872
Binney Cost per KG | 0.97549 |  | South Platte Cost per KG | 1.3367 | 530.9651 | Aurora Reservoir Cost per KG | 0.71276 | 121.7668 | [8 empty] | Ferric Chloride |  | 11272.1876 | 2.9248
[17 empty] | Hydrogen Peroxide |  | 744.9471 | 0.1567
Notes: | [16 empty] | Potassium Permanganate |  | 3052.6796 | 0.23816
1. The difference between the "Binney MG Produced" and the Net numbers is the ammont of water needed from distribution to create the finished water (W3 to Chlorine and NaOH Motive) | [16 empty] | Sodium Hydroxide |  | 24964.0057 | 7.1251
Note on B40: Peter Bong: 3% Solution Strength
Note on C40: Peter Bong: 40% Solution Strength
Note on D40: Peter Bong: 50% Solution Strength
Note on E40: Peter Bong: 100% Solution Strength, PEC Cost
Note on F40: Peter Bong: 0.5% Solution Strength
Note on G40: Peter Bong: 99% Solution Strength
Note on H40: Peter Bong: 35% Solution Strength
Note on I40: Peter Bong: 3% Solution Strength
Note on J40: Peter Bong: 40% Solution Strength
Note on K40: Peter Bong: 100% Solution Strength
Note on L40: Peter Bong: 5.5% Solution Strength
Note on M40: Peter Bong: 0.5% Solution Strength
Note on N40: Peter Bong: 0.5% Solution Strength
Note on O40: Peter Bong: 100% Solution Strength
Note on P40: Peter Bong: 100% Solution Strength
Note on Q40: Peter Bong: 100% Solution Strength
Note on R40: Peter Bong: 100% Solution Strength
Note on S40: Peter Bong: 40% Solution Strength
Note on T40: Peter Bong: 40% Solution Strength
Note on U40: Peter Bong: 100% Solution Strength
Note on V40: Peter Bong: 100% Solution Strength
Note on Y40: Peter Bong: 50% Solution Strength
Note on Z40: Peter Bong: 50% Solution Strength
Note on AB40: Peter Bong: 100% Solution Strength
Note on AC40: Peter Bong: 3% Solution Strength
Note on AJ40: Peter Bong: Cost per kW*Hr
Note on AK40: Peter Bong: Cost per kW*Hr
Note on AL40: Peter Bong: Cost per kW*Hr
Note on AM40: Peter Bong: Cost per kW*Hr
Note on AN40: Peter Bong: Cost per kW*Hr
Note on AO40: Peter Bong: Cost per kW*Hr
Note on AP40: Peter Bong: Cost per kW*Hr
Note on AQ40: Peter Bong: Cost per kW*Hr
Note on AR40: Peter Bong: Cost per kW*Hr
Note on AS40: Peter Bong: Cost per kW*Hr
Note on AI42: Peter Bong: See Utility Summary Seet For Data

## MARCH
Current Application Point |  | Notes: Chemical are arranged in general process flow
Not in Use
| South Platte | [6 empty] | Aurora Reservoir | [5 empty] | Filters/Adsorbers | [5 empty] | Finished Water | [6 empty] | From Chlorinator 5 | Valve Vault 1 (To Wemlinger RWAR) | RWAR Flow to Process | RWSP Flow to Process | Finished Water Flow | AR Net to Distribution | SP Net to Distribution | AR to Total Flow Blend | Blended&RW | Softening | Pre-Chem | Floc/Sed | UV/AOP | Filtration/Ad | Post-Chem | Finished | Recycle | Control | pass | bwpfyearly
| KMnO4 (RW) | FeCl3 (Rapid Mix & Flow Split) | NaOH (Rapid Mix) | PEC/PEA (Reactors) | PEA (Sludge) | CO2 (Post Softening) | H202 (UV) | KMnO4 (RW) | FeCl3 (Rapid Mix) | PEC (Rapid Mix) | PAC (Basin 1 & 2) | PEA (Basin 1 & 2) | PEA (Sludge) | PEN AR (FIC) | PEN SP (FIC) | PEN AR (Individual Filters) | PEN SP (Individual Filters) | FeCl3 AR (Backwash Supply) | FeCl3 SP (Backwash Supply) | Cl2 AR | Cl2 SP | NH3 AR (CCB Effluent) | NH3 SP (CCB Effluent) | NaOH AR (CCB Effluent) | NaOH SP (CCB Effluent) | Fluoride(CCB Effluent) | Cl2 to RWAR, RWSP, ARFIC, or SPFIC | KMnO4 (RWAR to Wemlinger) |  |  | Total Produced From Binney
| Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Gallons per Day | MGD | MGD | MGD | MGD | MGD | Ratio | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day
2019-03-01 |  | 76.9394 | 937.284 | 17.6854 | 0 | 2894.2756 | 28.2901 | 107.3259 | 346.2795 | 18.7954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.8285 | 151.4875 | 31.321 | 22.7208 | 61.9824 | 44.963 | 0 | 82.7254 | 0 | 8.5315 | 6.4447 | 13.7939 | 7.8081 | 5.6641 | 0.57957 | 300.7076 | 1304.0439 | 2944.0596 | 371.326 | 1234.8166 | 2558.2558 | 674.0941 | 1997.3774 | 495.4781 | 618.7842
2019-03-02 |  | 55.578 | 924.5301 | 17.5878 | 0 | 3215.7389 | 27.5339 | 107.5011 | 346.2633 | 19.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.0084 | 157.4975 | 31.909 | 23.9304 | 67.2552 | 50.4386 | 0 | 81.6852 | 0 | 8.52 | 6.2582 | 14.0267 | 7.924 | 5.9427 | 0.57144 | 325.0138 | 1331.7761 | 3044.5688 | 177.7565 | 1258.8463 | 2642.696 | 708.3658 | 1932.6729 | 544.6788 | 636.8109
2019-03-03 |  | 53.4839 | 889.7392 | 17.0269 | 0 | 3104.0158 | 26.4614 | 107.2746 | 345.5172 | 18.7962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.702 | 148.7622 | 32.4821 | 23.0428 | 75.2892 | 53.41 | 0 | 79.7239 | 0 | 8.502 | 6.0425 | 13.6912 | 7.9346 | 5.6288 | 0.585 | 336.7438 | 1352.1219 | 3156.8489 | 177.7565 | 1258.8463 | 2709.8843 | 787.3734 | 1926.8182 | 576.4263 | 636.6746
2019-03-04 |  | 61.9548 | 915.2332 | 17.2576 | 0 | 3102.3124 | 27.2012 | 117.9761 | 379.8576 | 20.7033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233.8825 | 157.2043 | 35.0834 | 23.5813 | 93.1445 | 62.6071 | 0 | 83.8728 | 0 | 9.3475 | 6.1912 | 14.9218 | 8.8213 | 5.9292 | 0.59803 | 332.3656 | 1337.3006 | 3211.7178 | 177.7565 | 1258.8463 | 2623.5649 | 779.5523 | 2039.0645 | 571.7672 | 645
2019-03-05 |  | 78.0531 | 1098.28 | 20.0436 | 0 | 3108.2831 | 32.6026 | 129.9798 | 418.8141 | 22.7316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261.226 | 145.8287 | 39.5958 | 22.1042 | 116.1308 | 64.8297 | 0 | 93.9926 | 0 | 10.3065 | 7.429 | 15.4866 | 9.8849 | 5.5182 | 0.64175 | 318.5005 | 1328.4508 | 3243.353 | 177.7565 | 1258.8463 | 2599.7156 | 751.7998 | 2107.1414 | 548.2083 | 618.3471
2019-03-06 |  | 52.8007 | 890.0397 | 16.399 | 0 | 2820.3965 | 26.4944 | 134.0419 | 423.8939 | 23.0588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254.9832 | 132.4549 | 38.8984 | 20.2064 | 121.8491 | 63.2964 | 0 | 79.4721 | 0 | 10.4256 | 6.0201 | 14.8825 | 9.6338 | 5.0044 | 0.65813 | 305.8753 | 1340.0238 | 2839.129 | 177.7565 | 1258.8463 | 2540.4146 | 711.6615 | 2088.7656 | 496.7973 | 592.7484
2019-03-07 |  | 47.9919 | 813.7267 | 14.4043 | 0 | 2568.2502 | 14.7791 | 152.9616 | 472.928 | 25.7837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.1809 | 65.3239 | 48.9072 | 9.5888 | 159.6614 | 31.3034 | 0 | 87.0047 | 0 | 12.9224 | 5.5042 | 15.0177 | 12.3242 | 2.4163 | 0.83608 | 294.2042 | 1355.5736 | 2831.7556 | 177.7565 | 1258.8463 | 2261.4388 | 635.683 | 2059.3594 | 438.081 | 636.882
2019-03-08 |  | 44.3447 | 745.1817 | 13.3219 | 0 | 3376.4077 | 19.0883 | 140.7564 | 431.7989 | 23.4945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318.1177 | 86.7937 | 47.4841 | 12.9553 | 158.596 | 43.2706 | 0 | 81.1902 | 0 | 12.2192 | 5.0406 | 15.108 | 11.7188 | 3.1973 | 0.78565 | 285.063 | 1408.9092 | 2832.8944 | 177.7565 | 1258.8463 | 2348.3111 | 635.0849 | 2039.4487 | 429.8934 | 644.1407
2019-03-09 |  | 43.5938 | 745.3799 | 13.3355 | 0 | 2709.5338 | 22.102 | 131.0696 | 366.8616 | 19.853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268.237 | 134.1263 | 40.3712 | 20.1867 | 128.1642 | 64.0858 | 0 | 73.8025 | 0 | 10.3801 | 5.0418 | 15.1202 | 9.92 | 4.9603 | 0.66665 | 293.3473 | 1422.5516 | 3074.0586 | 177.7565 | 1258.8463 | 2567.2602 | 626.2603 | 2051.1748 | 441.8856 | 561.5438
2019-03-10 |  | 43.771 | 749.132 | 13.318 | 0 | 2719.9843 | 22.1519 | 131.1362 | 367.0041 | 20.0922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258.1615 | 129.056 | 38.696 | 19.3443 | 123.7976 | 61.8869 | 0 | 73.7039 | 0 | 10.3869 | 5.0507 | 14.9469 | 9.7974 | 4.8978 | 0.66671 | 295.1542 | 1435.1651 | 2838.4818 | 177.7565 | 1258.8463 | 2586.3337 | 641.7047 | 2058.7659 | 432.3587 | 577.0408
2019-03-11 |  | 44.018 | 749.5491 | 13.205 | 0 | 2942.7884 | 22.0937 | 131.0061 | 366.9995 | 19.8554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260.5711 | 125.789 | 39.5518 | 19.0934 | 125.0728 | 60.3781 | 0 | 73.7043 | 0 | 10.3838 | 5.0479 | 14.909 | 9.8788 | 4.7689 | 0.67443 | 292.5121 | 1467.4626 | 3324.8462 | 177.7565 | 1258.8463 | 2602.8551 | 663.8153 | 2030.2184 | 427.3711 | 599.8002
2019-03-12 |  | 47.6887 | 818.2888 | 14.7093 | 0 | 3099.4616 | 24.1623 | 124.2855 | 333.7691 | 18.1409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.3885 | 144.6043 | 35.6657 | 21.5441 | 113.0549 | 68.2916 | 0 | 71.9647 | 0 | 9.4441 | 5.4767 | 14.7609 | 9.0667 | 5.4768 | 0.62342 | 277.4673 | 1484.3904 | 2881.8491 | 177.7565 | 1258.8463 | 2555.6087 | 622.7425 | 1960.7948 | 399.8578 | 690.9405
2019-03-13 |  | 51.2149 | 902.8528 | 16.4193 | 0 | 3706.0281 | 26.1002 | 126.345 | 333.038 | 18.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230.9856 | 156.8637 | 35.1537 | 23.873 | 110.5939 | 75.105 | 0 | 74.7344 | 0 | 9.4185 | 5.9532 | 14.8958 | 8.7347 | 5.9318 | 0.59556 | 314.968 | 1487.3294 | 2902.5616 | 177.7565 | 1258.8463 | 2681.1008 | 651.8731 | 2003.7339 | 475.0257 | 608.4711
2019-03-14 |  | 42.8377 | 672.3346 | 13.1379 | 0 | 2598.7199 | 21.7537 | 113.9552 | 296.2732 | 16.0866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203.4642 | 127.1252 | 30.1706 | 18.8507 | 99.1181 | 61.9294 | 0 | 64.8519 | 0 | 8.3825 | 4.9584 | 12.6522 | 7.6817 | 4.7996 | 0.61546 | 333.7759 | 1524.1641 | 2836.8955 | 177.7565 | 1258.8463 | 2684.1707 | 707.8568 | 1861.7228 | 517.3145 | 600.0516
2019-03-15 |  | 42.5755 | 706.8157 | 13.1219 | 0 | 2699.0397 | 21.6926 | 112.3106 | 291.8933 | 15.8914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.293 | 130.8634 | 31.1839 | 19.4982 | 100.5534 | 62.8725 | 0 | 65.0654 | 0 | 8.2594 | 4.9576 | 12.9927 | 7.9252 | 4.9554 | 0.61528 | 312.6835 | 1474.4745 | 2794.1342 | 177.7565 | 1258.8463 | 2589.1272 | 714.1038 | 1857.1444 | 473.937 | 567.3574
2019-03-16 |  | 42.4624 | 713.4786 | 13.1767 | 0 | 2917.1341 | 21.6974 | 112.1479 | 291.652 | 15.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.9524 | 131.8467 | 33.672 | 21.0452 | 100.4003 | 62.7509 | 0 | 65.2261 | 0 | 8.2527 | 4.9571 | 13.1101 | 7.9998 | 5 | 0.61538 | 302.6945 | 1452.3075 | 2826.4551 | 177.7565 | 1258.8463 | 2631.006 | 652.942 | 1852.0054 | 465.6276 | 546.0991
2019-03-17 |  | 42.3089 | 713.2337 | 13.1659 | 0 | 2802.017 | 21.7136 | 112.3152 | 291.7715 | 16.1763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.1672 | 130.7151 | 32.9967 | 20.6206 | 99.1145 | 61.9397 | 0 | 65.4232 | 0 | 8.2567 | 4.9564 | 13.0044 | 7.9284 | 4.9547 | 0.61541 | 292.9514 | 1431.4183 | 2842.2301 | 177.7565 | 1258.8463 | 2644.1004 | 633.8581 | 1834.7548 | 457.7126 | 533.2277
2019-03-18 |  | 48.94 | 820.1449 | 14.6702 | 0 | 2861.6845 | 17.3325 | 112.3249 | 291.8348 | 16.0847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206.1587 | 139.9705 | 32.1589 | 21.8341 | 97.7691 | 66.3799 | 0 | 68.0247 | 0 | 8.2583 | 5.5859 | 13.2075 | 7.7899 | 5.2889 | 0.59561 | 287.89 | 1351.1469 | 2837.0876 | 177.7565 | 1258.8463 | 2623.5071 | 624.4815 | 1883.1776 | 426.4845 | 601.0275
2019-03-19 |  | 80.1251 | 903.0163 | 15.3931 | 0 | 3472.787 | 26.2056 | 101.1433 | 291.9161 | 15.6715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211.5001 | 158.5763 | 33.7365 | 25.2946 | 97.0197 | 72.7424 | 0 | 69.6812 | 0 | 8.2592 | 5.9534 | 14.1288 | 8.0008 | 5.9988 | 0.5715 | 290.0313 | 1339.1989 | 2784.2704 | 177.7565 | 1258.8463 | 2644.5689 | 625.2222 | 1900.7539 | 420.5892 | 600.935
2019-03-20 |  | 60.7378 | 903.7108 | 15.7884 | 0 | 3278.9863 | 26.1118 | 98.9625 | 292.0719 | 16.0166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206.0065 | 154.5172 | 32.4679 | 24.3528 | 95.3043 | 71.4839 | 0 | 70.499 | 0 | 8.2651 | 5.9551 | 14.0029 | 7.9333 | 5.9505 | 0.57141 | 291.0239 | 1339.4367 | 2856.7103 | 177.7565 | 1258.8463 | 2670.0842 | 624.6339 | 1928.5549 | 420.7244 | 619.8271
2019-03-21 |  | 66.1849 | 905.0552 | 15.7389 | 0 | 3333.2478 | 26.2806 | 99.9641 | 294.901 | 16.2595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203.4694 | 152.5804 | 31.2829 | 23.4588 | 92.2311 | 69.1635 | 0 | 71.5776 | 0 | 8.3451 | 5.964 | 13.7896 | 7.8128 | 5.8588 | 0.57146 | 280.7382 | 1330.4721 | 2833.2189 | 177.7565 | 1258.8463 | 2636.3645 | 609.425 | 1902.9723 | 409.7324 | 663.2973
2019-03-22 |  | 52.5518 | 904.1133 | 15.7342 | 0 | 3361.0453 | 26.1736 | 100.0167 | 295.1168 | 16.1269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.015 | 152.929 | 31.305 | 23.4661 | 92.3016 | 69.189 | 0 | 71.2779 | 0 | 8.3514 | 5.9578 | 13.8236 | 7.8196 | 5.8615 | 0.57156 | 283.3709 | 1338.6225 | 3063.2256 | 177.7565 | 1258.8463 | 2653.2383 | 618.6356 | 1899.0487 | 408.4653 | 567.7164
2019-03-23 |  | 52.8099 | 904.2106 | 15.8075 | 0 | 3292.6465 | 26.116 | 97.4329 | 294.3585 | 15.8909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203.7332 | 152.805 | 31.3612 | 23.5217 | 95.3448 | 71.511 | 0 | 71.7362 | 0 | 8.3282 | 5.9585 | 13.8456 | 7.8264 | 5.87 | 0.57142 | 294.1356 | 1340.3312 | 2849.4496 | 177.7565 | 1258.8463 | 2655.1056 | 644.6797 | 1959.5901 | 428.019 | 548.614
2019-03-24 |  | 52.3173 | 903.4209 | 16.2521 | 0 | 3154.6354 | 26.0649 | 100.1267 | 315.2045 | 17.1011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.4672 | 149.175 | 34.1747 | 23.0192 | 103.9436 | 70.0139 | 0 | 73.6889 | 0 | 8.921 | 5.9531 | 14.3533 | 8.4929 | 5.7206 | 0.59752 | 289.2809 | 1334.8895 | 3017.6493 | 177.7565 | 1258.8463 | 2601.0922 | 624.1042 | 1977.1293 | 414.7779 | 549.7261
2019-03-25 |  | 51.9819 | 903.3228 | 16.2582 | 0 | 3134.4029 | 26.1075 | 106.8079 | 364.6827 | 19.9086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250.9833 | 150.581 | 39.9284 | 23.9556 | 121.776 | 73.0612 | 0 | 79.0923 | 0 | 10.3195 | 5.9533 | 16.0386 | 9.9289 | 5.957 | 0.62501 | 282.9137 | 1309.5313 | 2829.1773 | 177.7565 | 1258.8463 | 2632.8933 | 612.3734 | 2092.6469 | 407.5 | 579.5872
2019-03-26 |  | 51.7165 | 899.789 | 16.2774 | 0 | 3027.5519 | 26.1481 | 106.7997 | 364.6958 | 19.7876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249.1681 | 149.5234 | 38.9905 | 23.3978 | 121.1791 | 72.7184 | 0 | 79.0913 | 0 | 10.3194 | 5.9507 | 16.0132 | 9.9117 | 5.9479 | 0.62496 | 267.6092 | 1300.4724 | 2807.1232 | 177.7565 | 1258.8463 | 2588.4732 | 586.4561 | 2063.3201 | 368.1143 | 730.262
2019-03-27 |  | 51.4946 | 932.7897 | 16.2881 | 0 | 3006.109 | 26.2736 | 106.8099 | 364.5836 | 19.7306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251.2478 | 150.7558 | 39.4967 | 23.6992 | 122.0091 | 73.2089 | 0 | 79.0932 | 0 | 10.3183 | 5.952 | 16.1553 | 10.0004 | 6.0005 | 0.62499 | 262.0759 | 1309.694 | 2791.3898 | 177.7565 | 1258.8463 | 2551.5326 | 566.4972 | 2040.1843 | 356.0224 | 783.9073
2019-03-28 |  | 89.5982 | 924.139 | 15.7308 | 0 | 3066.5543 | 26.198 | 106.9049 | 364.6896 | 19.9004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247.4847 | 148.5158 | 39.2145 | 23.5327 | 117.32 | 70.4038 | 0 | 79.0929 | 0 | 10.3198 | 5.9558 | 15.8446 | 9.819 | 5.8924 | 0.62496 | 267.3437 | 1300.1561 | 3049.9883 | 177.7565 | 1258.8463 | 2538.4757 | 574.3845 | 2043.3311 | 361.7947 | 647.0392
2019-03-29 |  | 51.4946 | 932.7897 | 16.2881 | 0 | 3006.109 | 26.2736 | 106.8099 | 364.5836 | 19.7306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251.2478 | 150.7558 | 39.4967 | 23.6992 | 122.0091 | 73.2089 | 0 | 79.0932 | 0 | 10.3183 | 5.952 | 16.1553 | 10.0004 | 6.0005 | 0.62499 | 262.0759 | 1309.694 | 2791.3898 | 177.7565 | 1258.8463 | 2551.5326 | 566.4972 | 2040.1843 | 356.0224 | 783.9073
2019-03-30 |  | 51.4774 | 918.2951 | 15.7964 | 0 | 2866.0105 | 26.0533 | 109.5601 | 367.464 | 20.0229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244.0184 | 146.3454 | 39.6566 | 23.7833 | 109.2353 | 65.5118 | 0 | 79.1737 | 0 | 10.399 | 5.9482 | 15.5332 | 9.6062 | 5.7611 | 0.62511 | 305.0123 | 1324.4307 | 2781.434 | 177.7565 | 1258.8463 | 2666.4893 | 659.7839 | 2142.4734 | 440.4877 | 555.7698
2019-03-31 |  | 51.4653 | 918.2495 | 15.7918 | 0 | 2969.2356 | 26.1146 | 116.1344 | 369.8623 | 20.3495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.9536 | 148.1112 | 39.9664 | 23.97 | 112.2703 | 67.3345 | 0 | 79.9124 | 0 | 10.4648 | 5.9486 | 15.9175 | 9.8029 | 5.8793 | 0.6251 | 293.3597 | 1306.9158 | 2990.2797 | 177.7565 | 1258.8463 | 2650.0215 | 634.1518 | 2123.0452 | 409.6833 | 533.6974
Monthly Chemical/Power Usage | 0 | 1684.5125 | 26658.1268 | 479.1312 | 0 | 94215.3935 | 763.3722 | 3562.1867 | 10740.5801 | 585.0855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7317.6033 | 4361.4844 | 1126.3794 | 673.1715 | 3353.4913 | 1979.29 | 0 | 2349.1781 | 0 | Total MG | Total MG | Total MG | Total MG | Total MG | Overall Ratio | 9170.889 | 42472.4555 | 90708.2331 | 5704.0197 | 39000.2069 | 80489.2229 | 20170.0975 | 61697.3753 | 13820.8382 | 19079.2337
Cost per Gallon or lb or kW*Hr | 0.82128 | 1.4864 | 3.0825 | 3.9899 | 0 | 0.05795 | 3.739 | 0.82128 | 1.4864 | 3.9899 | 0 | 0 | 0 | 15.77 | 15.77 | 15.77 | 15.77 | 1.4864 | 1.4864 | 0.2996 | 0.2996 | 0.74349 | 0.74349 | 3.0825 | 3.0825 | 0 | 0.2996 | 0.82128 | 295.1268 | 178.319 | 452.1297 | 279.7278 | 167.0341 | 0.62612 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067
Cost Per Month | 0 | 2503.7832 | 82172.716 | 1911.6644 | 0 | 5459.7821 | 2854.2721 | 2925.5669 | 15964.3128 | 2334.4068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2192.3539 | 1306.7007 | 837.4567 | 500.4992 | 10337.0163 | 6101.09 | 0 | 703.8137 | 0 | [6 empty] | 614.4496 | 2845.6545 | 6077.4516 | 382.1693 | 2613.0139 | 5392.7779 | 1351.3965 | 4133.7241 | 925.9962 | 1278.3087
2019-03-02 | [33 empty] | Natural Gas | 360.1 | NA | 2471.97 | 977.77 | 1446.2 | 7289.11 | 1114.71 | NA | 186.86 | 524.96
Total Binney WPF Costs |  |  | South Platte Costs |  |  | Aurora Reservoir Costs |  |  | Labor Costs | [7 empty] | Monthly Truck Loads
Chemical | 138105.4348 |  | Chemical | 102810.5077 |  | Chemical | 34591.1134 |  | Monthly | 217325.23 | [6 empty] | Chemical |  | Gallon/Lbs | Loads
Electrical | 25614.9423 |  | Electrical | 13896.2745 |  | Electrical | 11718.6678 | [9 empty] | Ammonia |  | 1799.5509 | 0.4975
Natural Gas | 14371.68 |  | Natural Gas | 6314.7256 |  | Natural Gas | 8056.9544 |  | Material Costs | [7 empty] | Anionic Polymer |  | 0 | 0
Labor | 217325.23 |  | Labor | 108662.615 |  | Labor | 108662.615 |  | Monthly | 46279.67 | [6 empty] | Carbon Dioxide |  | 94215.3935 | 2.3554
Materials | 46279.67 |  | Materials | 23139.835 |  | Materials | 23139.835 | [9 empty] | Carbon PAC |  | 0 | 0
Binney MG Produced | 452.1297 |  | Net South Platte MG Produced | 167.0341 |  | Net Aurora Reservoir MG Produced | 279.7278 | [9 empty] | Cationic Polymer |  | 1064.2167 | 0.20512
Total Treated (MG) | 473.4458 |  | RWSP to Process (MG) | 178.319 |  | RWAR to Process (MG) | 295.1268
Binney Cost per MG | 932.9409 |  | South Platte Cost per MG | 1429.0339 | 615.5059 | Aurora Reservoir Cost per MG | 630.8109 | 123.6599 | [8 empty] | Chlorine |  | 14028.2657 | 0.87677
Binney Cost per KG | 0.93294 |  | South Platte Cost per KG | 1.429 |  | Aurora Reservoir Cost per KG | 0.63081 | [9 empty] | Ferric Chloride |  | 12425.0926 | 3.2239
[17 empty] | Hydrogen Peroxide |  | 763.3722 | 0.16058
Notes: | [16 empty] | Potassium Permanganate |  | 3562.1867 | 0.27791
1. The difference between the "Binney MG Produced" and the Net numbers is the ammont of water needed from distribution to create the finished water (W3 to Chlorine and NaOH Motive) | [16 empty] | Sodium Hydroxide |  | 31990.908 | 9.1306
Note on B40: Peter Bong: 3% Solution Strength
Note on C40: Peter Bong: 40% Solution Strength
Note on D40: Peter Bong: 50% Solution Strength
Note on E40: Peter Bong: 100% Solution Strength, PEC Cost
Note on F40: Peter Bong: 0.5% Solution Strength
Note on G40: Peter Bong: 99% Solution Strength
Note on H40: Peter Bong: 35% Solution Strength
Note on I40: Peter Bong: 3% Solution Strength
Note on J40: Peter Bong: 40% Solution Strength
Note on K40: Peter Bong: 100% Solution Strength
Note on L40: Peter Bong: 5.5% Solution Strength
Note on M40: Peter Bong: 0.5% Solution Strength
Note on N40: Peter Bong: 0.5% Solution Strength
Note on O40: Peter Bong: 100% Solution Strength
Note on P40: Peter Bong: 100% Solution Strength
Note on Q40: Peter Bong: 100% Solution Strength
Note on R40: Peter Bong: 100% Solution Strength
Note on S40: Peter Bong: 40% Solution Strength
Note on T40: Peter Bong: 40% Solution Strength
Note on U40: Peter Bong: 100% Solution Strength
Note on V40: Peter Bong: 100% Solution Strength
Note on Y40: Peter Bong: 50% Solution Strength
Note on Z40: Peter Bong: 50% Solution Strength
Note on AB40: Peter Bong: 100% Solution Strength
Note on AC40: Peter Bong: 3% Solution Strength
Note on AJ40: Peter Bong: Cost per kW*Hr
Note on AK40: Peter Bong: Cost per kW*Hr
Note on AL40: Peter Bong: Cost per kW*Hr
Note on AM40: Peter Bong: Cost per kW*Hr
Note on AN40: Peter Bong: Cost per kW*Hr
Note on AO40: Peter Bong: Cost per kW*Hr
Note on AP40: Peter Bong: Cost per kW*Hr
Note on AQ40: Peter Bong: Cost per kW*Hr
Note on AR40: Peter Bong: Cost per kW*Hr
Note on AS40: Peter Bong: Cost per kW*Hr
Note on AI42: Peter Bong: See Utility Summary Seet For Data

## APRIL
Current Application Point |  | Notes: Chemical are arranged in general process flow
Not in Use
| South Platte | [6 empty] | Aurora Reservoir | [5 empty] | Filters/Adsorbers | [5 empty] | Finished Water | [6 empty] | From Chlorinator 5 | Valve Vault 1 (To Wemlinger RWAR) | RWAR Flow to Process | RWSP Flow to Process | Finished Water Flow | AR Net to Distribution | SP Net to Distribution | AR to Total Flow Blend | Blended&RW | Softening | Pre-Chem | Floc/Sed | UV/AOP | Filtration/Ad | Post-Chem | Finished | Recycle | Control | pass | bwpfyearly
| KMnO4 (RW) | FeCl3 (Rapid Mix & Flow Split) | NaOH (Rapid Mix) | PEC/PEA (Reactors) | PEA (Sludge) | CO2 (Post Softening) | H202 (UV) | KMnO4 (RW) | FeCl3 (Rapid Mix) | PEC (Rapid Mix) | PAC (Basin 1 & 2) | PEA (Basin 1 & 2) | PEA (Sludge) | PEN AR (FIC) | PEN SP (FIC) | PEN AR (Individual Filters) | PEN SP (Individual Filters) | FeCl3 AR (Backwash Supply) | FeCl3 SP (Backwash Supply) | Cl2 AR | Cl2 SP | NH3 AR (CCB Effluent) | NH3 SP (CCB Effluent) | NaOH AR (CCB Effluent) | NaOH SP (CCB Effluent) | Fluoride(CCB Effluent) | Cl2 to RWAR, RWSP, ARFIC, or SPFIC | KMnO4 (RWAR to Wemlinger) |  |  | Total Produced From Binney
| Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Gallons per Day | MGD | MGD | MGD | MGD | MGD | Ratio | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day
2019-04-01 |  | 53.0526 | 918.5691 | 15.7983 | 0 | 3067.1431 | 26.0788 | 120.3945 | 368.0221 | 20.1254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251.4248 | 150.8437 | 40.3984 | 24.2373 | 113.1808 | 67.9035 | 0 | 75.9587 | 0 | 10.4145 | 5.9503 | 16.259 | 10.0009 | 6.0001 | 0.62502 | 287.672 | 1305.5085 | 2885.6283 | 177.7565 | 1258.8463 | 2544.0394 | 614.6154 | 2107.0036 | 433.7287 | 596.7524
2019-04-02 |  | 59.1251 | 918.2525 | 15.8233 | 0 | 3109.7605 | 26.126 | 121.1534 | 367.7705 | 20.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251.8587 | 151.1481 | 39.789 | 23.8786 | 110.3217 | 66.2074 | 0 | 74.3769 | 0 | 10.4064 | 5.9479 | 16.2575 | 9.9983 | 6.0003 | 0.62495 | 294.9967 | 1308.5077 | 3049.1138 | 177.7565 | 1258.8463 | 2513.309 | 601.1361 | 2078.2828 | 440.5541 | 565.3857
2019-04-03 |  | 62.9685 | 918.6726 | 15.8667 | 0 | 2985.9034 | 26.1534 | 121.1442 | 367.637 | 20.2305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256.0845 | 153.6239 | 40.0564 | 24.0296 | 109.2113 | 65.5154 | 0 | 74.3797 | 0 | 10.4029 | 5.9508 | 16.2555 | 10.0004 | 5.9992 | 0.62504 | 320.1773 | 1336.8125 | 2782.1733 | 177.7565 | 1258.8463 | 2503.284 | 592.114 | 2066.341 | 428.1281 | 634.0993
2019-04-04 |  | 63.1982 | 919.9311 | 15.7912 | 0 | 2993.0215 | 26.1134 | 121.0848 | 367.4814 | 20.2543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.0809 | 151.8392 | 39.7597 | 23.8544 | 110.0092 | 66.0015 | 0 | 74.6839 | 0 | 10.4002 | 5.9593 | 16.0898 | 9.8875 | 5.9321 | 0.62501 | 316.2007 | 1342.9207 | 2799.6465 | 177.7565 | 1258.8463 | 2473.1438 | 590.1244 | 2073.5696 | 424.7514 | 672.5356
2019-04-05 |  | 62.7793 | 919.6824 | 15.6816 | 0 | 3060.9862 | 25.9469 | 121.778 | 368.9133 | 20.2903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.441 | 146.6779 | 39.4409 | 22.8262 | 109.2737 | 63.2417 | 0 | 75.4451 | 0 | 10.4406 | 5.9572 | 15.8676 | 9.8837 | 5.7202 | 0.63341 | 309.9351 | 1343.5924 | 2753.7662 | 177.7565 | 1258.8463 | 2439.9043 | 576.3045 | 2030.9358 | 405.632 | 759.5158
2019-04-06 |  | 62.6614 | 919.2833 | 15.7952 | 0 | 3085.4161 | 25.9857 | 121.6758 | 369.1521 | 20.2611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252.9691 | 151.7712 | 39.6743 | 23.803 | 110.6096 | 66.3612 | 0 | 75.6855 | 0 | 10.4454 | 5.9549 | 16.0848 | 9.89 | 5.9336 | 0.62502 | 312.0377 | 1340.9464 | 3466.3983 | 177.7565 | 1258.8463 | 2416.727 | 574.5211 | 2055.7106 | 400.8547 | 610.5982
2019-04-07 |  | 62.845 | 919.0193 | 15.877 | 0 | 3086.584 | 26.0022 | 122.4209 | 371.3006 | 20.2389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250.3216 | 150.1903 | 38.9856 | 23.3909 | 107.7783 | 64.6659 | 0 | 75.4628 | 0 | 10.5069 | 5.9535 | 15.8294 | 9.7265 | 5.8358 | 0.625 | 326.7675 | 1364.6142 | 2834.6743 | 177.7565 | 1258.8463 | 2466.6082 | 571.2297 | 2052.5096 | 399.3813 | 608.4651
2019-04-08 |  | 62.8702 | 920.5041 | 16.2363 | 0 | 3087.2588 | 26.1138 | 122.1644 | 370.6098 | 20.2644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248.9914 | 149.3227 | 39.0909 | 23.4432 | 109.1856 | 65.4798 | 0 | 75.0924 | 0 | 10.4876 | 5.9629 | 15.8341 | 9.7485 | 5.8463 | 0.62511 | 317.1129 | 1356.5194 | 2824.4922 | 177.7565 | 1258.8463 | 2456.0245 | 605.4525 | 2048.2204 | 397.2801 | 686.9359
2019-04-09 |  | 64.1715 | 936.1376 | 16.195 | 0 | 3089.6075 | 26.6459 | 120.2676 | 365.1162 | 20.0669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251.2099 | 150.729 | 39.3971 | 23.6387 | 118.9112 | 71.3482 | 0 | 75.1823 | 0 | 10.3312 | 6.0639 | 16.1626 | 9.9997 | 5.9999 | 0.625 | 312.7935 | 1354.9883 | 3241.4152 | 177.7565 | 1258.8463 | 2454.8433 | 595.9804 | 2027.1025 | 389.1344 | 799.885
2019-04-10 |  | 64.5424 | 945.7682 | 16.2864 | 0 | 3110.165 | 26.8773 | 120.1995 | 365.065 | 19.8792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251.4397 | 150.8374 | 39.3263 | 23.5916 | 118.7603 | 71.2436 | 0 | 75.0326 | 0 | 10.3304 | 6.1263 | 16.1704 | 10.0011 | 5.9996 | 0.62504 | 316.935 | 1347.8938 | 3337.8403 | 177.7565 | 1258.8463 | 2553.712 | 612.7057 | 2049.5112 | 463.3532 | 622.8103
2019-04-11 |  | 65.484 | 946.957 | 16.2349 | 0 | 3087.6556 | 26.8875 | 120.3389 | 365.139 | 20.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242.5127 | 140.4568 | 38.2987 | 22.1816 | 115.4862 | 66.8865 | 0 | 75.0289 | 0 | 10.3316 | 6.1339 | 15.5897 | 9.7752 | 5.6615 | 0.63324 | 329.1183 | 1339.8846 | 3145.1357 | 177.7565 | 1258.8463 | 2649.3078 | 686.7637 | 2107.4308 | 496.2455 | 568.8037
2019-04-12 |  | 65.1484 | 945.7692 | 16.2603 | 0 | 2969.7878 | 26.8382 | 120.4893 | 365.3231 | 20.1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249.1365 | 149.4909 | 38.9931 | 23.3973 | 116.1646 | 69.7029 | 0 | 75.0317 | 0 | 10.338 | 6.1268 | 16.1701 | 10.0004 | 6.0006 | 0.62499 | 308.7471 | 1322.2294 | 2857.7444 | 177.7565 | 1258.8463 | 2605.5398 | 666.3113 | 2123.3955 | 480.3539 | 568.8231
2019-04-13 |  | 64.5665 | 945.8991 | 16.2608 | 0 | 2915.5822 | 26.7291 | 120.4661 | 365.3542 | 20.0727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249.4019 | 149.6312 | 39.3648 | 23.6173 | 113.2592 | 67.951 | 0 | 75.0335 | 0 | 10.3385 | 6.1268 | 16.0494 | 9.9273 | 5.956 | 0.62502 | 282.4902 | 1294.0465 | 3078.4 | 177.7565 | 1258.8463 | 2585.381 | 650.3183 | 2119.7607 | 473.4682 | 526.1797
2019-04-14 |  | 63.6294 | 934.9372 | 16.0309 | 0 | 2850.4099 | 26.4705 | 120.3651 | 365.2548 | 20.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255.2579 | 153.148 | 39.0747 | 23.4438 | 113.9809 | 68.3856 | 0 | 74.8738 | 0 | 10.336 | 6.0564 | 16.1617 | 10 | 5.9997 | 0.62501 | 267.2998 | 1282.0735 | 2836.2489 | 177.7565 | 1258.8463 | 2593.9803 | 613.8967 | 2099.4199 | 455.1287 | 570.7823
2019-04-15 |  | 62.8241 | 918.9748 | 15.8287 | 0 | 2856.2387 | 26.0746 | 121.393 | 368.6911 | 20.2353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270.2846 | 162.079 | 40.9738 | 24.5704 | 112.5445 | 67.4885 | 0 | 74.2247 | 0 | 10.4333 | 5.9528 | 15.9805 | 9.8901 | 5.9307 | 0.62513 | 244.3872 | 1268.626 | 2864.7399 | 177.7565 | 1258.8463 | 2466.4076 | 574.6111 | 2038.8403 | 416.1311 | 688.5694
2019-04-16 |  | 63.3842 | 915.1687 | 15.8458 | 0 | 2823.2525 | 26.0954 | 121.317 | 368.0499 | 20.1633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255.2954 | 153.1158 | 39.5057 | 23.6939 | 111.6496 | 66.9629 | 0 | 74.5735 | 0 | 10.4149 | 5.9555 | 15.5426 | 9.6395 | 5.7814 | 0.62509 | 243.469 | 1253.2513 | 2858.9956 | 177.7565 | 1258.8463 | 2497.8348 | 579.2608 | 2031.717 | 419.6155 | 667.2863
2019-04-17 |  | 62.7966 | 912.2697 | 15.8691 | 0 | 2769.7775 | 26.178 | 120.4944 | 365.4663 | 20.1052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254.235 | 138.6734 | 39.2815 | 21.4263 | 112.8951 | 61.579 | 0 | 74.3756 | 0 | 10.3415 | 5.9599 | 15.1471 | 9.6872 | 5.2839 | 0.64706 | 242.5549 | 1261.8229 | 3083.1808 | 177.7565 | 1258.8463 | 2432.0432 | 563.4343 | 1978.0112 | 402.2079 | 604.9063
2019-04-18 |  | 62.3716 | 906.6724 | 15.7984 | 0 | 2802.1981 | 26.099 | 121.0508 | 367.163 | 20.5885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.6369 | 155.7856 | 40.8642 | 24.519 | 115.6652 | 69.4006 | 0 | 74.3733 | 0 | 10.3889 | 5.9505 | 16.1722 | 9.9988 | 5.9994 | 0.62499 | 251.7486 | 1267.1444 | 2874.7706 | 177.7565 | 1258.8463 | 2411.7583 | 565.9806 | 2017.9492 | 427.3323 | 619.531
2019-04-20 |  | 62.3718 | 856.7601 | 15.8519 | 0 | 2586.3657 | 26.0265 | 123.0019 | 365.9422 | 20.4593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251.2318 | 150.7103 | 38.8702 | 23.3177 | 116.7645 | 70.0453 | 0 | 74.379 | 0 | 10.3552 | 5.9486 | 16.1576 | 10.0004 | 5.9991 | 0.62504 | 241.3233 | 1275.6679 | 2914.9189 | 405.1395 | 4147.5384 | 2407.5962 | 542.6732 | 1983.8188 | 399.3615 | 716.5822
2019-04-21 |  | 62.2715 | 856.1752 | 15.824 | 0 | 2619.4103 | 26.0499 | 127.1188 | 365.4538 | 20.4787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251.8589 | 151.1459 | 40.4263 | 24.2607 | 115.1573 | 69.1083 | 0 | 74.3839 | 0 | 10.3406 | 5.9492 | 16.047 | 9.9276 | 5.9578 | 0.62495 | 235.8417 | 1260.5536 | 2791.9148 | 506.2154 | 5547.2139 | 2352.2487 | 569.9999 | 1975.198 | 392.6922 | 595.9811
2019-04-22 |  | 62.1133 | 855.9526 | 15.8047 | 0 | 2606.7607 | 26.0317 | 127.1203 | 365.3672 | 20.4747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256.1957 | 153.7205 | 42.3358 | 25.402 | 112.6327 | 67.581 | 0 | 74.3795 | 0 | 10.3368 | 5.9483 | 16.1616 | 9.9995 | 5.9998 | 0.625 | 245.0604 | 1257.5898 | 2815.9993 | 506.2154 | 5547.2139 | 2507.6149 | 566.6918 | 2019.7864 | 442.7908 | 556.3553
2019-04-23 |  | 63.1663 | 856.5589 | 15.8166 | 0 | 2556.7331 | 26.1935 | 86.5594 | 365.4037 | 20.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.5245 | 152.1061 | 40.5603 | 24.3348 | 110.7988 | 66.4755 | 0 | 74.3773 | 0 | 10.3396 | 5.9521 | 15.9793 | 9.8883 | 5.9326 | 0.62501 | 237.3809 | 1249.3602 | 2897.2883 | 506.2154 | 5547.2139 | 2475.9184 | 571.1154 | 2032.0653 | 426.6925 | 667.8369
2019-04-24 |  | 62.9655 | 856.7553 | 15.8239 | 0 | 2499.744 | 26.1198 | 107.3174 | 407.4645 | 22.4089 | 0.0013218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268.2222 | 149.6322 | 43.1002 | 24.0442 | 123.0109 | 68.6237 | 0 | 85.4568 | 0 | 11.0454 | 5.9535 | 16.4732 | 10.4499 | 5.8296 | 0.6419 | 228.1472 | 1246.4832 | 2855.7428 | 506.2154 | 5547.2139 | 2510.0255 | 574.6956 | 2064.7722 | 405.2482 | 804.7775
2019-04-25 |  | 62.9214 | 857.0636 | 15.8177 | 0 | 2490.6837 | 26.0916 | 134.9132 | 433.7864 | 23.8923 | 0.00055704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270.9145 | 147.8355 | 43.7241 | 23.8599 | 130.7755 | 71.363 | 0 | 93.1781 | 0 | 12.274 | 5.9556 | 16.913 | 10.8044 | 5.8958 | 0.64696 | 223.3428 | 1243.2886 | 2866.8939 | 506.2154 | 5547.2139 | 2424.5659 | 576.4516 | 2066.1653 | 395.3372 | 637.4047
2019-04-26 |  | 62.987 | 831.2114 | 15.864 | 0 | 2393.1595 | 26.0123 | 155.3647 | 407.3902 | 22.3621 | 0.00014162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274.7377 | 144.6662 | 43.9999 | 23.1686 | 125.8429 | 66.264 | 0 | 88.9951 | 0 | 11.5277 | 5.9638 | 16.7396 | 10.7723 | 5.6723 | 0.65507 | 223.3715 | 1248.383 | 3047.8667 | 506.2154 | 5547.2139 | 2401.372 | 572.7736 | 2071.851 | 401.8509 | 709.6906
4/27/2019 |  | 62.7243 | 802.5445 | 15.8437 | 0 | 2261.2437 | 26.1819 | 155.6623 | 404.7936 | 21.8589 | 3.7766e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.1686 | 149.0224 | 43.6872 | 23.8328 | 125.7692 | 68.6112 | 0 | 88.3006 | 0 | 11.4552 | 5.9557 | 16.8837 | 10.7289 | 5.853 | 0.64703 | 225.8322 | 1244.5622 | 2910.4445 | 506.2154 | 5547.2139 | 2386.4033 | 593.6468 | 2079.5505 | 402.4006 | 678.2967
4/28/2019 |  | 62.3281 | 802.4096 | 15.745 | 0 | 2281.5334 | 26.1173 | 158.6426 | 404.6416 | 21.8217 | 2.8324e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277.9096 | 151.5694 | 44.2433 | 24.1299 | 127.3799 | 69.4719 | 0 | 88.3011 | 0 | 11.4503 | 5.9548 | 17.1881 | 10.9275 | 5.9598 | 0.64709 | 224.6321 | 1256.5641 | 2852.8689 | 558.2804 | 5547.2139 | 2404.2181 | 593.0788 | 2070.8968 | 409.6416 | 780.0589
4/27/2019 |  | 62.9182 | 798.9926 | 15.8535 | 0 | 2213.0235 | 26.1434 | 162.9103 | 404.5333 | 21.7881 | 5.6648e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279.8425 | 152.6798 | 45.3007 | 24.7157 | 127.0517 | 69.3184 | 0 | 88.2915 | 0 | 11.4477 | 5.9541 | 17.3004 | 10.9991 | 6.001 | 0.647 | 249.648 | 1259.4142 | 2823.6029 | 625.7906 | 5547.2139 | 2541.4878 | 596.5165 | 2104.0299 | 450.4355 | 557.8334
2019-04-29 |  | 62.9182 | 798.9926 | 15.8535 | 0 | 2213.0235 | 26.1434 | 162.9103 | 404.5333 | 21.7881 | 5.6648e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279.8425 | 152.6798 | 45.3007 | 24.7157 | 127.0517 | 69.3184 | 0 | 88.2915 | 0 | 11.4477 | 5.9541 | 17.3004 | 10.9991 | 6.001 | 0.647 | 249.648 | 1259.4142 | 2823.6029 | 625.7906 | 5547.2139 | 2541.4878 | 596.5165 | 2104.0299 | 450.4355 | 557.8334
2019-04-30 |  | 63.0765 | 748.321 | 15.8394 | 0 | 1917.1303 | 26.0204 | 162.905 | 404.5058 | 21.7464 | 5.6648e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272.726 | 148.7701 | 44.5281 | 24.2898 | 126.9992 | 69.2772 | 0 | 88.2904 | 0 | 11.4466 | 5.9536 | 17.2947 | 10.9998 | 6.0003 | 0.64704 | 265.7465 | 1272.5594 | 2800.9297 | 625.7906 | 5547.2139 | 2563.7634 | 641.4308 | 2155.6039 | 481.3705 | 556.508
Monthly Chemical/Power Usage | 0 | 1881.1812 | 26584.2059 | 477.4179 | 0 | 82389.5601 | 786.5478 | 3842.6239 | 11345.3253 | 622.565 | 0.0022565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7766.757 | 4513.9024 | 1228.3519 | 713.6147 | 3498.1214 | 2031.783 | 0 | 2355.4396 | 0 | Total MG | Total MG | Total MG | Total MG | Total MG | Overall Ratio | 8134.4181 | 38765.223 | 87976.4378 | 9583.9158 | 87826.1251 | 74580.5505 | 17830.3513 | 61833.4799 | 12811.5382 | 19191.0238
Cost per Gallon or lb or kW*Hr | 0.82128 | 1.4864 | 3.0825 | 4.3368 | 0 | 0.05795 | 3.739 | 0.82128 | 1.4864 | 4.3368 | 0 | 0 | 0 | 15.77 | 15.77 | 15.77 | 15.77 | 1.4864 | 1.4864 | 0.2996 | 0.2996 | 0.74349 | 0.74349 | 3.0825 | 3.0825 | 0 | 0.2996 | 0.82128 | 320.5558 | 179.5332 | 488.0625 | 304.5516 | 176.9824 | 0.63246 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063
Cost Per Month | 0 | 2796.1027 | 81944.8577 | 2070.4658 | 0 | 4774.475 | 2940.9263 | 3155.8855 | 16863.1787 | 2699.9399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2326.9204 | 1352.3652 | 913.2726 | 530.5685 | 10782.8332 | 6262.8979 | 0 | 705.6897 | 0 | [6 empty] | 512.4683 | 2442.2091 | 5542.5156 | 603.7867 | 5533.0459 | 4698.5747 | 1123.3121 | 3895.5092 | 807.1269 | 1209.0345
2019-04-02 | [33 empty] | Natural Gas | 1675.89 | NA | 1397.97 | 779.75 | 891.82 | 4901.24 | 2045.36 | NA | 153.59 | 760.22
Total Binney WPF Costs |  |  | South Platte Costs |  |  | Aurora Reservoir Costs |  |  | Labor Costs | [7 empty] | Monthly Truck Loads
Chemical | 140120.3791 |  | Chemical | 102672.659 |  | Chemical | 36742.0304 |  | Monthly | 149922.87 | [6 empty] | Chemical |  | Gallon/Lbs | Loads
Electrical | 26367.583 |  | Electrical | 15514.4643 |  | Electrical | 10853.1187 | [9 empty] | Ammonia |  | 1941.9666 | 0.53687
Natural Gas | 12605.84 |  | Natural Gas | 5216.8086 |  | Natural Gas | 7389.0314 |  | Material Costs | [7 empty] | Anionic Polymer |  | 0 | 0
Labor | 149922.87 |  | Labor | 74961.435 |  | Labor | 74961.435 |  | Monthly | 34232.68 | [6 empty] | Carbon Dioxide |  | 82389.5601 | 2.0597
Materials | 34232.68 |  | Materials | 17116.34 |  | Materials | 17116.34 | [9 empty] | Carbon PAC |  | 0.0022565 | 0.0022551
Binney MG Produced | 488.0625 |  | Net South Platte MG Produced | 176.9824 |  | Net Aurora Reservoir MG Produced | 304.5516 | [9 empty] | Cationic Polymer |  | 1099.9829 | 0.21202
Total Treated (MG) | 500.089 |  | RWSP to Process (MG) | 179.5332 |  | RWAR to Process (MG) | 320.5558
Binney Cost per MG | 726.3694 |  | South Platte Cost per MG | 1200.2332 |  | Aurora Reservoir Cost per MG | 458.7718 | [9 empty] | Chlorine |  | 14636.0991 | 0.91476
Binney Cost per KG | 0.72637 |  | South Platte Cost per KG | 1.2002 | 580.1293 | Aurora Reservoir Cost per KG | 0.45877 | 120.643 | [8 empty] | Ferric Chloride |  | 13226.5065 | 3.4318
[17 empty] | Hydrogen Peroxide |  | 786.5478 | 0.16545
Notes: | [16 empty] | Potassium Permanganate |  | 3842.6239 | 0.29979
1. The difference between the "Binney MG Produced" and the Net numbers is the ammont of water needed from distribution to create the finished water (W3 to Chlorine and NaOH Motive) | [16 empty] | Sodium Hydroxide |  | 32114.1103 | 9.1658
Note on B40: Peter Bong: 3% Solution Strength
Note on C40: Peter Bong: 40% Solution Strength
Note on D40: Peter Bong: 50% Solution Strength
Note on E40: Peter Bong: 100% Solution Strength, PEC Cost
Note on F40: Peter Bong: 0.5% Solution Strength
Note on G40: Peter Bong: 99% Solution Strength
Note on H40: Peter Bong: 35% Solution Strength
Note on I40: Peter Bong: 3% Solution Strength
Note on J40: Peter Bong: 40% Solution Strength
Note on K40: Peter Bong: 100% Solution Strength
Note on L40: Peter Bong: 5.5% Solution Strength
Note on M40: Peter Bong: 0.5% Solution Strength
Note on N40: Peter Bong: 0.5% Solution Strength
Note on O40: Peter Bong: 100% Solution Strength
Note on P40: Peter Bong: 100% Solution Strength
Note on Q40: Peter Bong: 100% Solution Strength
Note on R40: Peter Bong: 100% Solution Strength
Note on S40: Peter Bong: 40% Solution Strength
Note on T40: Peter Bong: 40% Solution Strength
Note on U40: Peter Bong: 100% Solution Strength
Note on V40: Peter Bong: 100% Solution Strength
Note on Y40: Peter Bong: 50% Solution Strength
Note on Z40: Peter Bong: 50% Solution Strength
Note on AB40: Peter Bong: 100% Solution Strength
Note on AC40: Peter Bong: 3% Solution Strength
Note on AJ40: Peter Bong: Cost per kW*Hr
Note on AK40: Peter Bong: Cost per kW*Hr
Note on AL40: Peter Bong: Cost per kW*Hr
Note on AM40: Peter Bong: Cost per kW*Hr
Note on AN40: Peter Bong: Cost per kW*Hr
Note on AO40: Peter Bong: Cost per kW*Hr
Note on AP40: Peter Bong: Cost per kW*Hr
Note on AQ40: Peter Bong: Cost per kW*Hr
Note on AR40: Peter Bong: Cost per kW*Hr
Note on AS40: Peter Bong: Cost per kW*Hr
Note on AI42: Peter Bong: See Utility Summary Seet For Data

## MAY
Current Application Point |  | Notes: Chemical are arranged in general process flow
Not in Use
| South Platte | [6 empty] | Aurora Reservoir | [5 empty] | Filters/Adsorbers | [5 empty] | Finished Water | [6 empty] | From Chlorinator 5 | Valve Vault 1 (To Wemlinger RWAR) | RWAR Flow to Process | RWSP Flow to Process | Finished Water Flow | AR Net to Distribution | SP Net to Distribution | AR to Total Flow Blend | Blended&RW | Softening | Pre-Chem | Floc/Sed | UV/AOP | Filtration/Ad | Post-Chem | Finished | Recycle | Control | pass | bwpfyearly
| KMnO4 (RW) | FeCl3 (Rapid Mix & Flow Split) | NaOH (Rapid Mix) | PEC/PEA (Reactors) | PEA (Sludge) | CO2 (Post Softening) | H202 (UV) | KMnO4 (RW) | FeCl3 (Rapid Mix) | PEC (Rapid Mix) | PAC (Basin 1 & 2) | PEA (Basin 1 & 2) | PEA (Sludge) | PEN AR (FIC) | PEN SP (FIC) | PEN AR (Individual Filters) | PEN SP (Individual Filters) | FeCl3 AR (Backwash Supply) | FeCl3 SP (Backwash Supply) | Cl2 AR | Cl2 SP | NH3 AR (CCB Effluent) | NH3 SP (CCB Effluent) | NaOH AR (CCB Effluent) | NaOH SP (CCB Effluent) | Fluoride(CCB Effluent) | Cl2 to RWAR, RWSP, ARFIC, or SPFIC | KMnO4 (RWAR to Wemlinger) |  |  | Total Produced From Binney
| Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Gallons per Day | MGD | MGD | MGD | MGD | MGD | Ratio | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day
2019-05-01 |  | 62.9519 | 761.1103 | 15.8085 | 0 | 1820.1044 | 26.196 | 122.5986 | 404.3262 | 22.2253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272.0922 | 148.4457 | 44.2692 | 24.152 | 125.4938 | 68.4658 | 0 | 88.2929 | 0 | 11.4415 | 5.9517 | 17.2882 | 10.9984 | 6.0004 | 0.64701 | 262.0634 | 1267.3895 | 2837.6766 | 625.7906 | 5547.2139 | 2616.1549 | 650.4018 | 2149.4458 | 475.631 | 571.5314
2019-05-02 |  | 62.9338 | 781.999 | 15.5474 | 0 | 1895.1821 | 26.232 | 110.4704 | 403.4224 | 22.1476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267.4357 | 145.8412 | 42.9864 | 23.4418 | 122.3547 | 66.7239 | 0 | 88.4017 | 0 | 11.4145 | 5.9556 | 16.9278 | 10.765 | 5.8705 | 0.64711 | 250.7161 | 1259.8922 | 2804.9269 | 625.7906 | 5547.2139 | 2536.8304 | 625.3935 | 2145.3888 | 443.9713 | 658.1747
2019-05-03 |  | 62.654 | 786.8582 | 15.2548 | 0 | 1985.5271 | 26.2854 | 135.2186 | 433.2633 | 23.7391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268.0891 | 147.2448 | 41.8778 | 23.0009 | 121.542 | 66.7555 | 0 | 92.6364 | 0 | 12.2559 | 5.955 | 16.7591 | 10.6248 | 5.8355 | 0.64548 | 234.7005 | 1255.2481 | 2843.2666 | 625.7906 | 5547.2139 | 2556.4789 | 648.3283 | 2098.7154 | 416.875 | 647.9837
2019-05-04 |  | 62.2677 | 783.9911 | 15.6934 | 0 | 1909.2721 | 26.7941 | 144.8302 | 409.602 | 22.5166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279.6345 | 134.9162 | 43.5564 | 21.0148 | 125.8426 | 60.7157 | 0 | 90.516 | 0 | 11.7669 | 6.0286 | 16.4795 | 10.9745 | 5.2949 | 0.67455 | 225.2966 | 1233.1213 | 2656.5291 | 246.0778 | 1742.7673 | 2544.4297 | 651.3713 | 2089.2781 | 344.8738 | 714.7487
2019-05-05 |  | 63.146 | 787.9059 | 15.8323 | 0 | 1922.9173 | 26.0373 | 166.5738 | 436.3731 | 23.9739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297.7926 | 148.9312 | 47.5333 | 23.7722 | 132.6861 | 66.3586 | 0 | 92.4065 | 0 | 12.3479 | 5.9634 | 18.1973 | 11.9998 | 6.0013 | 0.66661 | 234.963 | 1252.0063 | 2798.0011 | 432.4303 | 1100.4575 | 2435.7589 | 608.5585 | 2160.1923 | 333.9653 | 648.578
2019-05-06 |  | 62.945 | 787.7356 | 15.4214 | 0 | 1967.2458 | 26.3177 | 182.4058 | 435.8247 | 23.7271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292.6933 | 146.3555 | 46.1401 | 23.0714 | 123.848 | 61.9277 | 0 | 88.6931 | 0 | 12.3331 | 5.9614 | 17.7676 | 11.7223 | 5.8615 | 0.66665 | 227.7144 | 1249.613 | 2816.6351 | 474.655 | 1100.4575 | 2270.083 | 617.8322 | 2160.9887 | 333.2567 | 612.3301
2019-05-07 |  | 17.2502 | 215.608 | 5.6975 | 0 | 543.8283 | 7.2617 | 222.3686 | 587.9738 | 32.1773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399.9481 | 39.4539 | 65.1893 | 6.4308 | 182.2912 | 17.9826 | 0 | 76.8061 | 0 | 16.6329 | 1.6227 | 18.0129 | 16.2133 | 1.5994 | 0.91021 | 229.8773 | 1288.6503 | 1413.2499 | 474.655 | 1100.4575 | 2106.9277 | 599.4058 | 2156.218 | 405.7717 | 547.6908
2019-05-08 |  | 0 | 0 | 0.89472 | 0 | 0 | 0 | 237.4591 | 648.3831 | 35.5342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.4784 | 0 | 72.3095 | 0 | 203.7316 | 0 | 0 | 75.69 | 0 | 18.3324 | 0 | 18.1893 | 18 | 0 | 1 | 245.2974 | 1248.2752 | 898.3243 | 474.655 | 1100.4575 | 2132.8709 | 597.4091 | 2207.5104 | 478.3305 | 562.4609
2019-05-09 |  | 33.5231 | 407.8893 | 8.5789 | 0 | 1269.8696 | 12.487 | 237.0872 | 648.6544 | 35.5007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 423.821 | 0 | 70.7314 | 0 | 202.6774 | 0 | 0 | 92.9848 | 0 | 18.3492 | 3.1781 | 18.1176 | 17.9323 | 0 | 1 | 268.364 | 1260.0566 | 1883.4951 | 474.655 | 1100.4575 | 2242.3446 | 654.1296 | 2256.9338 | 472.3367 | 531.9678
2019-05-10 |  | 63.5661 | 711.4669 | 15.8294 | 0 | 2216.2269 | 26.1364 | 201.3643 | 531.2399 | 29.1134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353.7385 | 80.357 | 56.5237 | 12.8402 | 162.9441 | 37.0152 | 0 | 93.7613 | 0 | 15.0286 | 5.9611 | 17.6666 | 14.2552 | 3.2383 | 0.81489 | 261.2762 | 1267.3941 | 2737.2434 | 474.655 | 1100.4575 | 2417.0071 | 621.5096 | 2221.3917 | 416.3016 | 536.5351
2019-05-11 |  | 63.2435 | 778.4297 | 15.7937 | 0 | 1672.387 | 26.0209 | 179.6821 | 435.985 | 23.9209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301.0254 | 150.5471 | 48.1331 | 24.072 | 131.0118 | 65.5208 | 0 | 82.3878 | 0 | 12.3374 | 5.9476 | 18.0805 | 11.9225 | 5.9626 | 0.66662 | 247.3198 | 1263.6057 | 2786.7135 | 474.655 | 1100.4575 | 2438.4236 | 611.2515 | 2181.2596 | 375.1253 | 518.6065
2019-05-12 |  | 63.1139 | 809.29 | 15.7931 | 0 | 1884.0253 | 26.058 | 180.804 | 439.016 | 24.0809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296.5373 | 148.2762 | 47.3891 | 23.6958 | 126.8531 | 63.4298 | 0 | 82.7467 | 0 | 12.4222 | 5.9479 | 17.8331 | 11.7611 | 5.8808 | 0.66666 | 240.6346 | 1260.9519 | 2826.2837 | 474.655 | 1100.4575 | 2378.8315 | 602.3977 | 2162.3717 | 368.787 | 592.3118
2019-05-13 |  | 63.4462 | 843.8631 | 15.9399 | 0 | 1986.3163 | 26.264 | 184.3683 | 436.471 | 23.8109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300.124 | 150.0764 | 47.8984 | 23.9515 | 127.5245 | 63.7683 | 0 | 83.0525 | 0 | 12.3517 | 6.0012 | 18.0492 | 11.9052 | 5.9532 | 0.66665 | 234.979 | 1265.5171 | 2835.2706 | 474.655 | 1100.4575 | 2304.5725 | 616.1584 | 2145.1483 | 368.2968 | 708.6603
2019-05-14 |  | 64.102 | 817.1781 | 16.1321 | 0 | 1959.7014 | 26.5792 | 198.8997 | 462.9283 | 25.3867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318.2317 | 149.6881 | 50.3975 | 23.7057 | 142.5727 | 67.0625 | 0 | 85.948 | 0 | 13.0991 | 6.0741 | 18.9347 | 12.7577 | 6.0009 | 0.6801 | 237.7651 | 1271.3183 | 2832.4757 | 474.655 | 1100.4575 | 2333.4014 | 622.9707 | 2222.9346 | 362.1598 | 702.2108
2019-05-15 |  | 64.2215 | 794.3026 | 16.0972 | 0 | 1823.3097 | 26.6217 | 194.5487 | 472.162 | 25.8554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315.8675 | 146.5171 | 49.6659 | 23.0378 | 151.4728 | 70.2616 | 0 | 87.0734 | 0 | 13.3616 | 6.0716 | 18.7673 | 12.7093 | 5.8953 | 0.68313 | 231.8964 | 1269.9425 | 2884.6458 | 474.655 | 1100.4575 | 2357.1744 | 627.1122 | 2290.2128 | 364.3767 | 706.7737
2019-05-16 |  | 63.6432 | 787.7065 | 16.0124 | 0 | 1849.0609 | 26.2984 | 232.8803 | 541.0757 | 29.6781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390.7646 | 147.9893 | 62.5058 | 23.672 | 197.1032 | 74.6464 | 0 | 99.5339 | 0 | 16.2207 | 6.0212 | 21.8437 | 15.7086 | 5.9491 | 0.72531 | 241.1393 | 1273.3083 | 2925.851 | 474.655 | 1100.4575 | 2325.7024 | 553.4671 | 2609.3338 | 361.1719 | 736.1356
2019-05-17 |  | 64.0015 | 792.5681 | 16.1001 | 0 | 1860.976 | 26.6824 | 248.7588 | 520.1761 | 28.5215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396.8289 | 148.7967 | 64.5743 | 24.2131 | 192.7961 | 72.2917 | 0 | 100.3061 | 0 | 16.3563 | 6.0585 | 22.1997 | 16.0004 | 5.9996 | 0.72729 | 247.3383 | 1255.0988 | 2772.4764 | 474.655 | 1100.4575 | 2290.7831 | 529.9173 | 2618.394 | 372.6696 | 651.8692
2019-05-18 |  | 64.299 | 787.9232 | 16.0885 | 0 | 1865.0923 | 26.644 | 248.4076 | 519.4472 | 28.4468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401.9502 | 141.0892 | 62.5768 | 21.9652 | 182.9111 | 64.2039 | 0 | 99.6543 | 0 | 16.3326 | 6.0577 | 21.4538 | 15.7378 | 5.5242 | 0.74019 | 237.5734 | 1247.7728 | 2735.0361 | 474.655 | 1100.4575 | 2271.9307 | 507.6738 | 2590.3773 | 369.5516 | 471.4362
2019-05-19 |  | 63.7782 | 761.597 | 16.1248 | 0 | 1713.1019 | 26.7742 | 248.3142 | 519.1387 | 28.4381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396.6564 | 148.7064 | 64.0559 | 24.0146 | 186.5645 | 69.943 | 0 | 99.5808 | 0 | 16.3239 | 6.0785 | 22.0838 | 15.9173 | 5.9674 | 0.72733 | 247.0622 | 1257.0529 | 2734.1893 | 474.655 | 1100.4575 | 2353.2609 | 501.4413 | 2658.6585 | 407.4982 | 464.9743
2019-05-20 |  | 64.3432 | 760.5138 | 16.1714 | 0 | 1668.1679 | 26.7987 | 245.8751 | 514.0731 | 28.1355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375.7521 | 142.8229 | 59.7539 | 22.7124 | 187.3511 | 71.2119 | 0 | 99.0969 | 0 | 16.1634 | 6.087 | 21.5863 | 15.4907 | 5.888 | 0.72459 | 254.5637 | 1262.8115 | 2699.3705 | 474.655 | 1100.4575 | 2450.5967 | 523.6062 | 2664.6485 | 438.2262 | 492.5686
2019-05-21 |  | 63.0445 | 741.1519 | 15.901 | 0 | 1647.3048 | 26.3448 | 196.1957 | 404.9058 | 21.9533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291.2439 | 141.2375 | 45.4464 | 22.0391 | 148.0319 | 71.7875 | 0 | 84.9943 | 0 | 12.6981 | 5.9935 | 18.2117 | 12.1364 | 5.8855 | 0.67343 | 270.0036 | 1283.1816 | 2652.4614 | 474.655 | 1100.4575 | 2443.4945 | 554.6087 | 2360.9618 | 472.3637 | 533.4664
2019-05-22 |  | 63.0375 | 737.6447 | 15.8493 | 0 | 1623.8297 | 26.1272 | 170.3322 | 341.0124 | 18.5444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266.1485 | 154.829 | 40.9951 | 23.8484 | 122.2059 | 71.092 | 0 | 75.7845 | 0 | 10.7048 | 5.9668 | 16.1746 | 10.1258 | 5.8906 | 0.63222 | 257.6798 | 1267.5885 | 2666.1242 | 474.655 | 1100.4575 | 2426.1968 | 536.0204 | 2073.0695 | 456.454 | 563.2265
2019-05-23 |  | 63.5285 | 742.2206 | 15.9045 | 0 | 1624.2715 | 26.3637 | 191.7278 | 392.6229 | 21.4457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303.0016 | 151.5377 | 48.0943 | 24.053 | 143.2752 | 71.655 | 0 | 82.3769 | 0 | 12.3446 | 6.004 | 18.1853 | 11.9985 | 6.0007 | 0.66661 | 256.2378 | 1263.3376 | 2679.6352 | 474.655 | 1100.4575 | 2425.5257 | 533.5361 | 2200.342 | 478.1303 | 544.9861
2019-05-24 |  | 64.0197 | 743.9833 | 15.9907 | 0 | 1563.9404 | 26.5307 | 191.7116 | 392.5976 | 21.5307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286.7201 | 143.0655 | 44.4024 | 22.1556 | 138.4169 | 69.0662 | 0 | 82.3774 | 0 | 12.3422 | 6.018 | 17.4751 | 11.5414 | 5.7589 | 0.66712 | 248.1032 | 1267.8229 | 2677.8566 | 474.655 | 1100.4575 | 2394.9382 | 517.2293 | 2194.8915 | 455.7708 | 677.2719
2019-05-25 |  | 63.5114 | 744.2169 | 15.9814 | 0 | 1588.1134 | 26.4814 | 191.5539 | 392.2861 | 21.4968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294.4187 | 147.4224 | 46.0332 | 23.0499 | 142.4701 | 71.3382 | 0 | 82.3842 | 0 | 12.3351 | 6.0198 | 17.8179 | 11.7207 | 5.8688 | 0.66635 | 235.2389 | 1254.0664 | 2750.6846 | 474.655 | 1100.4575 | 2420.7379 | 498.5282 | 2249.4558 | 432.5663 | 679.0814
2019-05-26 |  | 63.3672 | 742.1143 | 15.8883 | 0 | 1563.4004 | 26.1225 | 191.4931 | 392.2566 | 21.4508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.5022 | 134.0216 | 45.4959 | 20.7747 | 147.3138 | 67.2677 | 0 | 82.122 | 0 | 12.3322 | 5.975 | 17.3018 | 11.748 | 5.3645 | 0.68652 | 227.5469 | 1252.7238 | 2723.648 | 474.655 | 1100.4575 | 2287.2141 | 515.8381 | 2121.2792 | 403.8702 | 604.1267
2019-05-27 |  | 63.6809 | 743.5724 | 15.8192 | 0 | 1455.6082 | 26.101 | 191.6076 | 392.1756 | 21.4403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297.5142 | 148.7585 | 46.282 | 23.1412 | 150.4128 | 75.2071 | 0 | 81.7237 | 0 | 12.3313 | 5.9517 | 18.1906 | 12.0005 | 6.0003 | 0.66666 | 230.742 | 1255.1038 | 2752.2269 | 474.655 | 1100.4575 | 2310.175 | 521.3369 | 2157.2974 | 403.5079 | 643.6031
2019-05-28 |  | 63.4043 | 742.2323 | 15.813 | 0 | 1463.0118 | 26.0453 | 191.5533 | 392.2249 | 21.4077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295.5425 | 147.7732 | 45.93 | 22.9653 | 147.3224 | 73.6622 | 0 | 81.721 | 0 | 12.3329 | 5.9518 | 18.0046 | 11.8791 | 5.9396 | 0.66666 | 239.471 | 1255.1005 | 2753.6156 | 423.7123 | 1100.4575 | 2393.6488 | 510.855 | 2160.8832 | 413.6246 | 543.2355
2019-05-29 |  | 63.1069 | 735.9021 | 15.8103 | 0 | 1482.8869 | 26.1852 | 192.5593 | 394.2922 | 21.5629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290.9951 | 146.1638 | 45.5786 | 22.8936 | 145.2408 | 72.9529 | 0 | 81.8537 | 0 | 12.3982 | 5.9528 | 17.8657 | 11.7164 | 5.885 | 0.66565 | 247.3747 | 1265.7987 | 2709.5899 | 400.2559 | 1100.4575 | 2453.0432 | 506.2956 | 2194.8288 | 436.8466 | 541.9662
2019-05-30 |  | 62.6685 | 736.1394 | 15.8242 | 0 | 1595.4569 | 26.2388 | 192.6222 | 394.3976 | 21.5913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270.9146 | 135.5032 | 42.1756 | 21.095 | 136.9736 | 68.51 | 0 | 82.481 | 0 | 12.3998 | 5.9552 | 16.5436 | 10.835 | 5.4193 | 0.66659 | 234.0656 | 1258.3839 | 2788.5588 | 449.601 | 3483.6895 | 2411.1786 | 508.369 | 2080.9377 | 428.4091 | 764.7996
2019-05-31 |  | 62.8965 | 738.3195 | 15.8407 | 0 | 1673.413 | 26.3051 | 205.6344 | 433.6485 | 23.7207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.1004 | 148.1752 | 50.8414 | 23.031 | 166.9355 | 75.6212 | 0 | 88.2899 | 0 | 13.6356 | 5.9719 | 19.5229 | 13.2418 | 5.9985 | 0.68823 | 223.4278 | 1253.4017 | 2891.4342 | 477.003 | 4823.3522 | 2442.1991 | 526.7252 | 2299.629 | 440.3949 | 743.6296
Monthly Chemical/Power Usage | 0 | 1825.696 | 22105.4339 | 459.4341 | 0 | 51093.5493 | 757.3349 | 6029.9065 | 14121.956 | 773.0748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10002.5635 | 4064.5426 | 1589.3428 | 641.8111 | 4718.171 | 1916.445 | 0 | 2705.6778 | 0 | Total MG | Total MG | Total MG | Total MG | Total MG | Overall Ratio | 7530.4322 | 39085.5359 | 81767.4963 | 14748.8615 | 54202.8871 | 73771.9155 | 17699.6786 | 69882.9781 | 12731.1154 | 18916.9412
Cost per Gallon or lb or kW*Hr | 0.82128 | 1.4864 | 3.0825 | 4.3368 | 0 | 0.05795 | 3.739 | 0.82128 | 1.4864 | 4.3368 | 0 | 0 | 0 | 15.77 | 15.77 | 15.77 | 15.77 | 1.4864 | 1.4864 | 0.2996 | 0.2996 | 0.74349 | 0.74349 | 3.0825 | 3.0825 | 0 | 0.2996 | 0.82128 | 420.7266 | 172.6834 | 554.2439 | 402.3399 | 162.7347 | 0.71201 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067
Cost Per Month | 0 | 2713.632 | 68139.2041 | 1992.474 | 0 | 2960.8712 | 2831.6982 | 4952.2657 | 20990.2371 | 3352.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2996.768 | 1217.737 | 1181.6673 | 477.1829 | 14543.5923 | 5907.3727 | 0 | 810.6211 | 0 | [6 empty] | 504.539 | 2618.7309 | 5478.4222 | 988.1737 | 3631.5934 | 4942.7183 | 1185.8785 | 4682.1595 | 852.9847 | 1267.4351
2019-05-02 | [33 empty] | Natural Gas | 813.66 | NA | 1256.72 | 706.37 | 700.84 | 2805.81 | 738.5 | NA | 56.08 | 311.68
Total Binney WPF Costs |  |  | South Platte Costs |  |  | Aurora Reservoir Costs |  |  | Labor Costs | [7 empty] | Monthly Truck Loads
Chemical | 135067.9947 |  | Chemical | 86240.1721 |  | Chemical | 48017.2015 |  | Monthly | 136626.64 | [6 empty] | Chemical |  | Gallon/Lbs | Loads
Electrical | 26152.6354 |  | Electrical | 13308.4141 |  | Electrical | 12844.2213 | [9 empty] | Ammonia |  | 2231.1538 | 0.61681
Natural Gas | 7389.66 |  | Natural Gas | 2768.1228 |  | Natural Gas | 4621.5372 |  | Material Costs | [7 empty] | Anionic Polymer |  | 0 | 0
Labor | 136626.64 |  | Labor | 68313.32 |  | Labor | 68313.32 |  | Monthly | 81695.66 | [6 empty] | Carbon Dioxide |  | 51093.5493 | 1.2773
Materials | 81695.66 |  | Materials | 40847.83 |  | Materials | 40847.83 | [9 empty] | Carbon PAC |  | 0 | 0
Binney MG Produced | 554.2439 |  | Net South Platte MG Produced | 162.7347 |  | Net Aurora Reservoir MG Produced | 402.3399 | [9 empty] | Cationic Polymer |  | 1232.509 | 0.23756
Total Treated (MG) | 593.41 |  | RWSP to Process | 172.6834 |  | RWAR to Process | 420.7266
Binney Cost per MG | 652.0493 |  | South Platte Cost per MG | 1224.6567 | 529.9434 | Aurora Reservoir Cost per MG | 415.1012 | 119.3449 | [8 empty] | Chlorine |  | 16772.7839 | 1.0483
Binney Cost per KG | 0.65205 |  | South Platte Cost per KG | 1.2247 |  | Aurora Reservoir Cost per KG | 0.4151 | [9 empty] | Ferric Chloride |  | 15947.6521 | 4.1379
[17 empty] | Hydrogen Peroxide |  | 757.3349 | 0.15931
Notes: | [16 empty] | Potassium Permanganate |  | 6029.9065 | 0.47043
1. The difference between the "Binney MG Produced" and the Net numbers is the ammont of water needed from distribution to create the finished water (W3 to Chlorine and NaOH Motive) | [16 empty] | Sodium Hydroxide |  | 28740.0499 | 8.2028
Note on B40: Peter Bong: 3% Solution Strength
Note on C40: Peter Bong: 40% Solution Strength
Note on D40: Peter Bong: 50% Solution Strength
Note on E40: Peter Bong: 100% Solution Strength, PEC Cost
Note on F40: Peter Bong: 0.5% Solution Strength
Note on G40: Peter Bong: 99% Solution Strength
Note on H40: Peter Bong: 35% Solution Strength
Note on I40: Peter Bong: 3% Solution Strength
Note on J40: Peter Bong: 40% Solution Strength
Note on K40: Peter Bong: 100% Solution Strength
Note on L40: Peter Bong: 5.5% Solution Strength
Note on M40: Peter Bong: 0.5% Solution Strength
Note on N40: Peter Bong: 0.5% Solution Strength
Note on O40: Peter Bong: 100% Solution Strength
Note on P40: Peter Bong: 100% Solution Strength
Note on Q40: Peter Bong: 100% Solution Strength
Note on R40: Peter Bong: 100% Solution Strength
Note on S40: Peter Bong: 40% Solution Strength
Note on T40: Peter Bong: 40% Solution Strength
Note on U40: Peter Bong: 100% Solution Strength
Note on V40: Peter Bong: 100% Solution Strength
Note on Y40: Peter Bong: 50% Solution Strength
Note on Z40: Peter Bong: 50% Solution Strength
Note on AB40: Peter Bong: 100% Solution Strength
Note on AC40: Peter Bong: 3% Solution Strength
Note on AJ40: Peter Bong: Cost per kW*Hr
Note on AK40: Peter Bong: Cost per kW*Hr
Note on AL40: Peter Bong: Cost per kW*Hr
Note on AM40: Peter Bong: Cost per kW*Hr
Note on AN40: Peter Bong: Cost per kW*Hr
Note on AO40: Peter Bong: Cost per kW*Hr
Note on AP40: Peter Bong: Cost per kW*Hr
Note on AQ40: Peter Bong: Cost per kW*Hr
Note on AR40: Peter Bong: Cost per kW*Hr
Note on AS40: Peter Bong: Cost per kW*Hr
Note on AI42: Peter Bong: See Utility Summary Seet For Data

## JUNE
Current Application Point |  | Notes: Chemical are arranged in general process flow
Not in Use
| South Platte | [6 empty] | Aurora Reservoir | [5 empty] | Filters/Adsorbers | [5 empty] | Finished Water | [6 empty] | From Chlorinator 5 | Valve Vault 1 (To Wemlinger RWAR) | RWAR Flow to Process | RWSP Flow to Process | Finished Water Flow | AR Net to Distribution | SP Net to Distribution | AR to Total Flow Blend | Blended&RW | Softening | Pre-Chem | Floc/Sed | UV/AOP | Filtration/Ad | Post-Chem | Finished | Recycle | Control | pass | bwpfyearly
| KMnO4 (RW) | FeCl3 (Rapid Mix & Flow Split) | NaOH (Rapid Mix) | PEC/PEA (Reactors) | PEA (Sludge) | CO2 (Post Softening) | H202 (UV) | KMnO4 (RW) | FeCl3 (Rapid Mix) | PEC (Rapid Mix) | PAC (Basin 1 & 2) | PEA (Basin 1 & 2) | PEA (Sludge) | PEN AR (FIC) | PEN SP (FIC) | PEN AR (Individual Filters) | PEN SP (Individual Filters) | FeCl3 AR (Backwash Supply) | FeCl3 SP (Backwash Supply) | Cl2 AR | Cl2 SP | NH3 AR (CCB Effluent) | NH3 SP (CCB Effluent) | NaOH AR (CCB Effluent) | NaOH SP (CCB Effluent) | Fluoride(CCB Effluent) | Cl2 to RWAR, RWSP, ARFIC, or SPFIC | KMnO4 (RWAR to Wemlinger) |  |  | Total Produced From Binney
| Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Gallons per Day | MGD | MGD | MGD | MGD | MGD | Ratio | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day
2019-06-01 |  | 63.6902 | 727.7742 | 15.8803 | 0 | 1614.9883 | 26.2151 | 224.7818 | 491.0194 | 26.9139 | 3.7766e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366.1576 | 146.4271 | 57.7797 | 23.1062 | 189.6113 | 75.8259 | 0 | 95.5496 | 0 | 15.4376 | 5.9724 | 21.2974 | 15.0013 | 5.9991 | 0.71434 | 223.7937 | 1254.96 | 2861.7597 | 477.003 | 4823.3522 | 2366.4053 | 552.1891 | 2520.4757 | 448.5762 | 677.4516
2019-06-02 |  | 62.9575 | 724.4738 | 15.8895 | 0 | 1475.0766 | 26.2556 | 225.5989 | 492.8756 | 26.957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359.2844 | 143.6737 | 56.7111 | 22.6781 | 185.2628 | 74.0845 | 0 | 95.7932 | 0 | 15.4954 | 5.9773 | 20.9696 | 14.7689 | 5.9059 | 0.71434 | 227.8257 | 1255.7248 | 2967.7347 | 477.003 | 4823.3522 | 2382.4533 | 542.8078 | 2511.3132 | 449.0188 | 690.9185
2019-06-03 |  | 63.0953 | 705.4864 | 15.8694 | 0 | 1408.9328 | 26.24 | 193.2421 | 430.6578 | 23.1167 | 3.7766e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307.0283 | 116.5746 | 49.0588 | 18.627 | 155.1906 | 58.9238 | 0 | 86.942 | 0 | 13.2702 | 5.9748 | 17.3143 | 12.3004 | 4.6703 | 0.7248 | 226.3505 | 1254.7914 | 2894.4744 | 436.1703 | 4515.6341 | 2221.627 | 551.8669 | 2338.3798 | 459.3455 | 785.255
2019-06-04 |  | 63.1373 | 706.8647 | 15.8186 | 0 | 1221.3057 | 26.1867 | 200.2884 | 453.9297 | 24.2903 | 6.609e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322.3355 | 113.6221 | 52.5697 | 18.5306 | 167.2999 | 58.9726 | 0 | 88.6937 | 0 | 13.7618 | 5.9709 | 17.7463 | 12.9421 | 4.562 | 0.73937 | 225.2456 | 1258.9579 | 2913.6194 | 410.6384 | 4326.8767 | 2174.0375 | 546.8711 | 2429.2624 | 454.0163 | 796.5948
2019-06-05 |  | 62.5171 | 712.1123 | 15.9004 | 0 | 1276.6747 | 26.2105 | 270.9088 | 587.2847 | 32.1262 | 9.4414e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 432.4681 | 144.1537 | 70.9027 | 23.6339 | 238.6029 | 79.533 | 0 | 108.2168 | 0 | 18.4541 | 5.9811 | 24.315 | 17.9995 | 5.9997 | 0.75 | 226.0043 | 1263.8295 | 2842.3964 | 410.6384 | 4326.8767 | 2311.7045 | 556.4563 | 3235.3464 | 461.7716 | 757.5304
2019-06-06 |  | 62.7108 | 710.8432 | 15.9261 | 0 | 1278.4507 | 26.3438 | 250.1034 | 534.4773 | 29.227 | 9.4414e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384.4983 | 141.9211 | 61.6529 | 22.7565 | 211.2359 | 77.9687 | 0 | 101.4296 | 0 | 16.8006 | 5.9708 | 22.1895 | 15.986 | 5.9006 | 0.7304 | 228.4596 | 1271.8862 | 2957.3963 | 410.6384 | 4326.8767 | 2317.3673 | 571.8893 | 3163.1747 | 454.8285 | 752.6699
2019-06-07 |  | 62.6118 | 709.9252 | 15.8776 | 0 | 1318.1858 | 26.2134 | 147.0204 | 307.3288 | 15.2027 | 5.6648e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228.2829 | 99.7726 | 34.8657 | 15.2383 | 115.3825 | 50.4287 | 0 | 70.8291 | 0 | 9.5277 | 5.9636 | 13.1218 | 9.0067 | 3.9364 | 0.69587 | 240.4313 | 1287.6994 | 2972.8856 | 410.6384 | 4326.8767 | 2212.5538 | 584.8899 | 1890.4393 | 578.0351 | 823.5823
2019-06-08 |  | 62.4152 | 715.9682 | 15.9489 | 0 | 1355.4412 | 26.2456 | 238.3026 | 487.8613 | 23.3817 | 1.8883e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362.326 | 145.6501 | 56.7043 | 22.7943 | 182.9075 | 73.5263 | 0 | 95.513 | 0 | 15.3405 | 5.9862 | 20.6415 | 14.5911 | 5.8654 | 0.71327 | 248.8519 | 1275.2062 | 2941.4196 | 410.6384 | 4326.8767 | 2560.8109 | 582.1085 | 2876.7233 | 493.2739 | 766.0025
2019-06-09 |  | 63.5595 | 712.582 | 15.9068 | 0 | 1323.9325 | 26.2633 | 238.4375 | 488.0805 | 26.771 | 1.8883e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372.2133 | 148.8914 | 59.8657 | 23.9473 | 188.2031 | 75.2843 | 0 | 95.5403 | 0 | 15.3473 | 5.9844 | 21.2115 | 14.999 | 5.9998 | 0.71428 | 228.9364 | 1248.2417 | 2801.1585 | 410.6384 | 4326.8767 | 2552.7568 | 535.7804 | 2824.949 | 416.7163 | 606.0945
2019-06-10 |  | 63.2773 | 702.7846 | 15.9229 | 0 | 1295.4728 | 26.256 | 248.0808 | 507.9103 | 27.792 | 9.4414e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386.7561 | 135.8252 | 62.3602 | 21.9003 | 194.3035 | 68.2376 | 0 | 97.6531 | 0 | 15.9755 | 5.9895 | 21.1463 | 15.4984 | 5.4429 | 0.74009 | 232.8368 | 1254.3683 | 2803.3559 | 412.2687 | 4198.3364 | 2460.755 | 541.4604 | 2869.571 | 433.8201 | 748.4963
2019-06-11 |  | 63.1414 | 698.1155 | 15.9692 | 0 | 1284.6378 | 26.3031 | 274.8999 | 563.1246 | 30.8329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425.0178 | 147.0372 | 69.0641 | 23.8931 | 214.33 | 74.1486 | 0 | 104.7293 | 0 | 17.7018 | 5.9963 | 23.2439 | 17.0924 | 5.9132 | 0.74297 | 231.3706 | 1264.2593 | 2917.5691 | 496.8286 | 4113.3842 | 2335.9509 | 575.9696 | 3142.4081 | 431.6612 | 722.2071
2019-06-12 |  | 63.5969 | 697.2729 | 15.99 | 0 | 1353.8457 | 26.2387 | 268.2353 | 584.0934 | 31.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430.7506 | 128.3 | 70.5255 | 21.0062 | 225.5057 | 67.1674 | 0 | 108.8631 | 0 | 18.3628 | 5.9887 | 23.3213 | 17.8021 | 5.3024 | 0.7705 | 243.2087 | 1266.822 | 2943.2906 | 406.3967 | 4113.3842 | 2340.2848 | 581.9795 | 3134.1768 | 419.43 | 678.4571
2019-06-13 |  | 62.7278 | 700.553 | 15.953 | 0 | 1358.4365 | 26.2338 | 304.5269 | 683.3182 | 37.4459 | 9.4414e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 494.6382 | 141.4599 | 80.0842 | 22.903 | 269.4925 | 77.0712 | 0 | 121.0259 | 0 | 21.4836 | 5.9887 | 26.6502 | 20.5154 | 5.8671 | 0.77761 | 232.4265 | 1278.488 | 3011.5912 | 414.0837 | 4113.3842 | 2429.2385 | 590.6663 | 3484.2262 | 532.7756 | 801.78
2019-06-14 |  | 63.5311 | 704.0992 | 15.8551 | 0 | 1380.6518 | 26.2345 | 303.1037 | 696.1133 | 38.1484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 519.9957 | 131.6075 | 84.3249 | 21.3421 | 303.0296 | 76.6948 | 0 | 122.64 | 0 | 21.889 | 5.9802 | 27.2233 | 21.4981 | 5.441 | 0.79803 | 231.223 | 1251.0334 | 3006.4669 | 430.5553 | 4113.3842 | 2589.3766 | 596.6665 | 3427.0641 | 612.9066 | 824.6094
2019-06-15 |  | 63.5549 | 704.8967 | 15.6691 | 0 | 1324.7293 | 26.4165 | 302.6286 | 681.0124 | 37.2493 | 1.8883e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 499.2258 | 142.6516 | 82.2046 | 23.4896 | 306.2464 | 87.5086 | 0 | 120.2665 | 0 | 21.4127 | 5.9871 | 26.9918 | 20.7678 | 5.9343 | 0.77776 | 240.3259 | 1281.1422 | 2963.1124 | 363.7677 | 4113.3842 | 2579.2919 | 585.1801 | 3411.2029 | 507.3739 | 756.7
2019-06-16 |  | 63.6093 | 705.008 | 15.6635 | 0 | 1295.3272 | 26.3251 | 307.8035 | 684.7617 | 37.5323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508.4268 | 146.69 | 80.9956 | 23.3686 | 303.8876 | 87.6769 | 0 | 120.8029 | 0 | 21.532 | 5.988 | 26.8392 | 20.5209 | 5.9206 | 0.77609 | 244.2452 | 1270.1874 | 2926.8236 | 363.7677 | 4113.3842 | 2558.9066 | 573.314 | 3441.8175 | 436.0594 | 717.6895
2019-06-17 |  | 63.7254 | 704.4305 | 15.6667 | 0 | 1248.8663 | 26.2358 | 285.4789 | 685.3625 | 37.5149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 516.3929 | 147.5645 | 82.6185 | 23.6091 | 302.7808 | 86.5227 | 0 | 120.9222 | 0 | 21.5508 | 5.9837 | 26.8559 | 20.5567 | 5.8743 | 0.77775 | 233.5702 | 1263.8661 | 2789.0285 | 363.7677 | 4113.3842 | 2596.1706 | 548.3468 | 3448.027 | 434.9459 | 690.654
2019-06-18 |  | 62.8773 | 705.3827 | 15.6497 | 0 | 1295.88 | 26.4051 | 237.4311 | 619.6337 | 33.8905 | 4.7207e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459.193 | 145.4375 | 73.5648 | 23.2997 | 275.6087 | 87.2919 | 0 | 112.5693 | 0 | 19.48 | 5.9904 | 25.0936 | 18.7707 | 5.9451 | 0.75946 | 225.4629 | 1254.6 | 2763.3321 | 363.7677 | 4113.3842 | 2614.4301 | 551.6565 | 3237.2353 | 446.9561 | 700.3537
2019-06-19 |  | 62.734 | 706.0232 | 15.6714 | 0 | 1317.7024 | 26.2482 | 228.6904 | 604.5582 | 33.0227 | 9.4414e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 439.0974 | 143.6305 | 69.5978 | 22.7657 | 260.9139 | 85.346 | 0 | 110.2053 | 0 | 19.0013 | 5.9963 | 24.1349 | 17.9068 | 5.8574 | 0.75352 | 231.1013 | 1266.5097 | 2797.6391 | 363.7677 | 4113.3842 | 2643.8127 | 554.897 | 2941.4652 | 451.5492 | 747.0248
2019-06-20 |  | 63.4623 | 706.3558 | 15.8943 | 0 | 1406.7472 | 26.3552 | 211.485 | 641.8583 | 35.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 466.7425 | 130.7521 | 75.0864 | 21.0345 | 271.6869 | 76.1097 | 0 | 127.3374 | 0 | 20.1815 | 5.9988 | 24.384 | 18.7487 | 5.2522 | 0.78117 | 242.3153 | 1227.4405 | 2895.0517 | 363.7677 | 4113.3842 | 2636.6876 | 576.8439 | 3041.6161 | 512.8439 | 767.4025
2019-06-21 |  | 63.1073 | 705.5409 | 15.9466 | 0 | 1446.1747 | 26.2742 | 163.8689 | 511.4766 | 27.9651 | 9.4414e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.8612 | 147.703 | 59.4307 | 23.1087 | 220.7623 | 85.8399 | 0 | 111.6298 | 0 | 16.0787 | 5.9925 | 21.3316 | 15.1007 | 5.8717 | 0.72003 | 246.6818 | 1026.7792 | 2863.7711 | 363.7677 | 4113.3842 | 2668.8711 | 570.54 | 2828.8336 | 548.682 | 622.9716
2019-06-22 |  | 62.6782 | 704.69 | 15.9648 | 0 | 1443.8825 | 26.339 | 112.2274 | 389.0281 | 21.2875 | 9.4414e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300.1581 | 152.3931 | 45.6675 | 23.1858 | 165.2815 | 83.915 | 0 | 92.2314 | 0 | 12.2307 | 5.9848 | 17.7606 | 11.6047 | 5.8918 | 0.66326 | 241.8861 | 1032.9025 | 2733.0741 | 383.5162 | 4225.7894 | 2715.0635 | 520.6507 | 2247.9198 | 446.5703 | 600.9148
2019-06-23 |  | 63.7471 | 696.87 | 15.9787 | 0 | 1339.6384 | 26.3463 | 103.8723 | 361.0234 | 19.786 | 6.609e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284.7231 | 155.3044 | 43.0275 | 23.4697 | 151.0535 | 82.3933 | 0 | 88.3134 | 0 | 11.3515 | 5.9844 | 17.1846 | 11.0007 | 6.0004 | 0.64706 | 241.8664 | 1035.5488 | 2736.7249 | 485.379 | 5002.7443 | 2725.7612 | 531.3959 | 2058.0269 | 436.882 | 572.8155
2019-06-24 |  | 64.1113 | 680.8756 | 15.9363 | 0 | 1215.2727 | 26.2047 | 113.0588 | 383.9951 | 20.9171 | 9.4414e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294.3795 | 149.8955 | 44.6942 | 22.7579 | 150.844 | 76.8084 | 0 | 91.563 | 0 | 12.0729 | 5.9826 | 17.3832 | 11.3825 | 5.7959 | 0.66261 | 227.5679 | 1034.673 | 2774.8519 | 485.379 | 5002.7443 | 2663.0496 | 536.7487 | 2257.7436 | 415.4692 | 754.8435
2019-06-25 |  | 63.8729 | 659.3113 | 15.9356 | 0 | 1235.7608 | 26.3273 | 115.6849 | 392.0557 | 21.3656 | 2.8324e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306.4551 | 153.2132 | 46.7567 | 23.3762 | 156.656 | 78.3206 | 0 | 92.9301 | 0 | 12.3262 | 5.9823 | 17.9246 | 11.8432 | 5.9211 | 0.66669 | 239.4172 | 1039.4678 | 2863.2464 | 485.379 | 5002.7443 | 2672.8477 | 532.7993 | 2631.9218 | 422.0669 | 766.5942
2019-06-26 |  | 63.6342 | 652.3801 | 15.9426 | 0 | 1337.7057 | 26.2658 | 118.5433 | 392.3276 | 21.4369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307.4634 | 153.7375 | 47.1434 | 23.5726 | 159.0064 | 79.5062 | 0 | 92.9269 | 0 | 12.3348 | 5.9816 | 18.1797 | 11.9993 | 5.9999 | 0.66666 | 228.1149 | 1035.8205 | 2925.4961 | 485.379 | 5002.7443 | 2665.6444 | 525.7567 | 2616.3632 | 534.9871 | 783.22
2019-06-27 |  | 63.3753 | 644.1076 | 15.9317 | 0 | 1358.5733 | 26.282 | 131.0755 | 392.314 | 21.4292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307.5122 | 153.7588 | 47.374 | 23.6874 | 159.8529 | 79.9278 | 0 | 92.9304 | 0 | 12.3355 | 5.9817 | 18.1793 | 11.9988 | 5.9995 | 0.66666 | 233.0718 | 1060.5774 | 2966.7752 | 485.379 | 5002.7443 | 2710.6949 | 562.8062 | 2606.628 | 744.2731 | 842.3447
2019-06-28 |  | 63.6132 | 650.3124 | 15.9926 | 0 | 1502.2366 | 26.2918 | 131.7995 | 392.2875 | 21.4727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302.0567 | 151.0621 | 46.3325 | 23.1714 | 156.9403 | 78.4877 | 0 | 92.9344 | 0 | 12.3332 | 5.9893 | 17.8506 | 11.7743 | 5.8885 | 0.66662 | 238.8506 | 1064.2265 | 3051.242 | 485.379 | 5002.7443 | 2704.8422 | 550.1036 | 2635.028 | 745.8157 | 896.0878
2019-06-29 |  | 63.9233 | 644.9091 | 15.983 | 0 | 1607.9729 | 26.3947 | 131.659 | 392.4238 | 21.4657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305.1792 | 139.8563 | 46.4129 | 21.2699 | 158.4115 | 72.5962 | 0 | 92.9344 | 0 | 12.3377 | 5.9834 | 17.5064 | 11.8728 | 5.441 | 0.68574 | 236.0898 | 1070.074 | 3086.0714 | 485.379 | 5002.7443 | 2678.2459 | 580.2 | 2612.3293 | 650.1425 | 838.2918
2019-06-30 |  | 63.6387 | 624.1077 | 15.9906 | 0 | 1663.6752 | 26.1554 | 128.5315 | 392.4327 | 21.4788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305.5259 | 152.7555 | 46.9369 | 23.4673 | 165.4832 | 82.7375 | 0 | 92.9356 | 0 | 12.337 | 5.9794 | 18.0421 | 11.9182 | 5.9588 | 0.66668 | 236.4486 | 1072.887 | 3153.523 | 485.379 | 5002.7443 | 2636.0848 | 570.6669 | 2647.6507 | 566.5373 | 843.9764
Monthly Chemical/Power Usage | 0 | 1898.6339 | 20824.0569 | 476.5249 | 0 | 40986.1783 | 788.3072 | 6211.369 | 15224.6265 | 827.0448 | 0.00055704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11374.1457 | 4251.3218 | 1804.3133 | 670.991 | 6205.7738 | 2298.8561 | 0 | 3046.8517 | 0 | Total MG | Total MG | Total MG | Total MG | Total MG | Overall Ratio | 7033.9807 | 35722.9705 | 87124.8816 | 12827.0616 | 133816.9043 | 75725.727 | 16783.508 | 84511.319 | 14947.3304 | 22333.5342
Cost per Gallon or lb or kW*Hr | 0.82128 | 1.4864 | 3.0825 | 4.3368 | 0 | 0.05795 | 3.739 | 0.82128 | 1.4864 | 4.3368 | 0 | 0 | 0 | 15.77 | 15.77 | 15.77 | 15.77 | 1.4864 | 1.4864 | 0.2996 | 0.2996 | 0.74349 | 0.74349 | 3.0825 | 3.0825 | 0 | 0.2996 | 0.82128 | 477.7445 | 179.5112 | 636.034 | 457.7684 | 170.3585 | 0.72878 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064
Cost Per Month | 0 | 2822.0436 | 64189.4058 | 2066.5933 | 0 | 2375.149 | 2947.5046 | 5101.298 | 22629.1966 | 3586.7277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3407.694 | 1273.696 | 1341.4967 | 498.878 | 19129.0744 | 7086.1411 | 0 | 912.8368 | 0 | [6 empty] | 450.1748 | 2286.2701 | 5575.9924 | 820.9319 | 8564.2819 | 4846.4465 | 1074.1445 | 5408.7244 | 956.6291 | 1429.3462
2019-06-02 | [33 empty] | Natural Gas | 677.07 | NA | 535.49 | 324.65 | 486.19 | 2110.49 | 598.45 | NA | 46.29 | 275.36
Total Binney WPF Costs |  |  | South Platte Costs |  |  | Aurora Reservoir Costs |  |  | Labor Costs | [7 empty] | Monthly Truck Loads
Chemical | 139367.7356 |  | Chemical | 83259.4114 |  | Chemical | 55195.4874 |  | Monthly | 147914.11 | [6 empty] | Chemical |  | Gallon/Lbs | Loads
Electrical | 31412.9419 |  | Electrical | 18026.33 |  | Electrical | 13386.6119 | [9 empty] | Ammonia |  | 2475.3043 | 0.68431
Natural Gas | 5053.99 |  | Natural Gas | 1833.1024 |  | Natural Gas | 3220.8876 |  | Material Costs | [7 empty] | Anionic Polymer |  | 0 | 0
Labor | 147914.11 |  | Labor | 73957.055 |  | Labor | 73957.055 |  | Monthly | 80211.03 | [6 empty] | Carbon Dioxide |  | 40986.1783 | 1.0247
Materials | 80211.03 |  | Materials | 40105.515 |  | Materials | 40105.515 | [9 empty] | Carbon PAC |  | 0.00055704 | 0.0005567
Binney MG Produced | 636.034 |  | Net South Platte MG Produced | 170.3585 | 488.7306 | Net Aurora Reservoir MG Produced | 457.7684 | 120.5751 | [8 empty] | Cationic Polymer |  | 1303.5697 | 0.25126
Total Treated (MG) | 657.2557 |  | RWSP to Process (MG) | 179.5112 |  | RWAR to Process (MG) | 477.7445
Binney Cost per MG | 614.6159 |  | South Platte Cost per MG | 1209.8491 |  | Aurora Reservoir Cost per MG | 389.048 | [9 empty] | Chlorine |  | 18672.3192 | 1.167
Binney Cost per KG | 0.61462 |  | South Platte Cost per KG | 1.2098 |  | Aurora Reservoir Cost per KG | 0.38905 | [9 empty] | Ferric Chloride |  | 17123.2604 | 4.4429
[17 empty] | Hydrogen Peroxide |  | 788.3072 | 0.16582
Notes: | [16 empty] | Potassium Permanganate |  | 6211.369 | 0.48459
1. The difference between the "Binney MG Produced" and the Net numbers is the ammont of water needed from distribution to create the finished water (W3 to Chlorine and NaOH Motive) | [16 empty] | Sodium Hydroxide |  | 29328.6868 | 8.3708
Note on B40: Peter Bong: 3% Solution Strength
Note on C40: Peter Bong: 40% Solution Strength
Note on D40: Peter Bong: 50% Solution Strength
Note on E40: Peter Bong: 100% Solution Strength, PEC Cost
Note on F40: Peter Bong: 0.5% Solution Strength
Note on G40: Peter Bong: 99% Solution Strength
Note on H40: Peter Bong: 35% Solution Strength
Note on I40: Peter Bong: 3% Solution Strength
Note on J40: Peter Bong: 40% Solution Strength
Note on K40: Peter Bong: 100% Solution Strength
Note on L40: Peter Bong: 5.5% Solution Strength
Note on M40: Peter Bong: 0.5% Solution Strength
Note on N40: Peter Bong: 0.5% Solution Strength
Note on O40: Peter Bong: 100% Solution Strength
Note on P40: Peter Bong: 100% Solution Strength
Note on Q40: Peter Bong: 100% Solution Strength
Note on R40: Peter Bong: 100% Solution Strength
Note on S40: Peter Bong: 40% Solution Strength
Note on T40: Peter Bong: 40% Solution Strength
Note on U40: Peter Bong: 100% Solution Strength
Note on V40: Peter Bong: 100% Solution Strength
Note on Y40: Peter Bong: 50% Solution Strength
Note on Z40: Peter Bong: 50% Solution Strength
Note on AB40: Peter Bong: 100% Solution Strength
Note on AC40: Peter Bong: 3% Solution Strength
Note on AJ40: Peter Bong: Cost per kW*Hr
Note on AK40: Peter Bong: Cost per kW*Hr
Note on AL40: Peter Bong: Cost per kW*Hr
Note on AM40: Peter Bong: Cost per kW*Hr
Note on AN40: Peter Bong: Cost per kW*Hr
Note on AO40: Peter Bong: Cost per kW*Hr
Note on AP40: Peter Bong: Cost per kW*Hr
Note on AQ40: Peter Bong: Cost per kW*Hr
Note on AR40: Peter Bong: Cost per kW*Hr
Note on AS40: Peter Bong: Cost per kW*Hr
Note on AI42: Peter Bong: See Utility Summary Seet For Data
Note on AN42: Linder, Kevin: estimated

## JULY
Current Application Point |  | Notes: Chemical are arranged in general process flow
Not in Use
| South Platte | [6 empty] | Aurora Reservoir | [5 empty] | Filters/Adsorbers | [5 empty] | Finished Water | [6 empty] | From Chlorinator 5 | Valve Vault 1 (To Wemlinger RWAR) | RWAR Flow to Process | RWSP Flow to Process | Finished Water Flow | AR Net to Distribution | SP Net to Distribution | AR to Total Flow Blend | Blended&RW | Softening | Pre-Chem | Floc/Sed | UV/AOP | Filtration/Ad | Post-Chem | Finished | Recycle | Control | pass | bwpfyearly
| KMnO4 (RW) | FeCl3 (Rapid Mix & Flow Split) | NaOH (Rapid Mix) | PEC/PEA (Reactors) | PEA (Sludge) | CO2 (Post Softening) | H202 (UV) | KMnO4 (RW) | FeCl3 (Rapid Mix) | PEC (Rapid Mix) | PAC (Basin 1 & 2) | PEA (Basin 1 & 2) | PEA (Sludge) | PEN AR (FIC) | PEN SP (FIC) | PEN AR (Individual Filters) | PEN SP (Individual Filters) | FeCl3 AR (Backwash Supply) | FeCl3 SP (Backwash Supply) | Cl2 AR | Cl2 SP | NH3 AR (CCB Effluent) | NH3 SP (CCB Effluent) | NaOH AR (CCB Effluent) | NaOH SP (CCB Effluent) | Fluoride(CCB Effluent) | Cl2 to RWAR, RWSP, ARFIC, or SPFIC | KMnO4 (RWAR to Wemlinger) |  |  | Total Produced From Binney
| Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Gallons per Day | MGD | MGD | MGD | MGD | MGD | Ratio | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day
2019-07-01 |  | 62.8214 | 606.332 | 15.9486 | 0 | 1702.3361 | 26.296 | 127.9715 | 392.3957 | 21.3642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305.1207 | 152.573 | 47.5974 | 23.8006 | 174.0852 | 87.0498 | 0 | 92.9343 | 0 | 12.339 | 5.9794 | 18.044 | 11.9101 | 5.9555 | 0.66665 | 249.2312 | 1080.4607 | 2992.991 | 485.379 | 5002.7443 | 2689.4738 | 569.7457 | 2635.4036 | 474.1651 | 840.524
2019-07-02 |  | 63.9358 | 606.3232 | 15.9192 | 0 | 1759.2994 | 26.2767 | 127.5645 | 392.3493 | 21.4298 | 9.4414e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307.9932 | 153.9763 | 47.7359 | 23.8648 | 177.436 | 88.7063 | 0 | 92.9384 | 0 | 12.3377 | 5.9802 | 18.1759 | 12.0002 | 5.9993 | 0.6667 | 239.8553 | 1078.4711 | 3024.9258 | 497.5128 | 5002.7443 | 2594.0599 | 588.6011 | 2653.2425 | 443.5172 | 766.4912
2019-07-03 |  | 63.4506 | 606.3716 | 15.8949 | 0 | 1627.4986 | 26.262 | 128.7108 | 395.5042 | 21.6207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319.9357 | 159.9298 | 44.4633 | 22.2264 | 184.3362 | 92.1462 | 0 | 93.346 | 0 | 12.4359 | 5.9806 | 17.503 | 11.5422 | 5.7697 | 0.66672 | 244.2419 | 1085.3992 | 3035.1525 | 565.1633 | 5002.7443 | 2668.6094 | 569.825 | 2668.5538 | 559.5214 | 824.1989
2019-07-04 |  | 62.9526 | 606.0754 | 15.9326 | 0 | 1414.4547 | 26.2452 | 130.7884 | 392.9305 | 21.4655 | 1.8883e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365.166 | 182.5923 | 47.0182 | 23.5103 | 216.2014 | 108.1062 | 0 | 93.5606 | 0 | 12.3532 | 5.9778 | 18.068 | 11.9209 | 5.9608 | 0.66666 | 241.7593 | 1097.7586 | 2955.8654 | 565.1633 | 5002.7443 | 2683.5309 | 624.2901 | 2693.0119 | 728.3916 | 775.3822
2019-07-05 |  | 62.5085 | 606.1982 | 15.8943 | 0 | 1365.3171 | 26.2907 | 138.1747 | 393.4386 | 21.5787 | 9.4414e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364.9892 | 182.5364 | 47.6885 | 23.8497 | 203.9835 | 102.0151 | 0 | 93.601 | 0 | 12.349 | 5.9787 | 18.1868 | 11.9996 | 6.0012 | 0.66662 | 246.524 | 1080.7516 | 3026.1485 | 565.1633 | 5002.7443 | 2674.8701 | 600.6402 | 2606.4495 | 490.0501 | 757.3053
2019-07-06 |  | 62.0783 | 615.672 | 15.8727 | 0 | 1362.6126 | 26.1315 | 143.9922 | 392.9228 | 21.4783 | 8.4972e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363.9733 | 181.9967 | 48.4751 | 24.2389 | 194.8367 | 97.4237 | 0 | 93.5978 | 0 | 12.3565 | 5.9673 | 18.0073 | 11.8875 | 5.9441 | 0.66665 | 251.883 | 1084.6504 | 2927.6593 | 565.1633 | 5002.7443 | 2677.8826 | 591.9095 | 2627.7658 | 517.067 | 721.9889
2019-07-07 |  | 62.7912 | 620.2103 | 15.8844 | 0 | 1330.2524 | 26.1297 | 149.1154 | 396.8448 | 21.8145 | 0.00017939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364.1975 | 181.9631 | 48.1843 | 24.0742 | 201.551 | 100.7004 | 0 | 93.6038 | 0 | 12.4763 | 5.963 | 18.0362 | 11.8862 | 5.9387 | 0.66683 | 247.6401 | 1090.5156 | 3058.5268 | 524.1601 | 5002.7443 | 2686.3386 | 602.041 | 2657.9312 | 672.6091 | 758.7856
2019-07-08 |  | 63.3868 | 621.5923 | 15.9281 | 0 | 1294.2035 | 26.3082 | 148.1147 | 393.5067 | 21.5659 | 0.0001605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.7906 | 171.7269 | 46.647 | 22.5148 | 187.643 | 90.5683 | 0 | 93.3172 | 0 | 12.3725 | 5.9763 | 17.3936 | 11.5875 | 5.5928 | 0.67446 | 244.9355 | 1081.2652 | 3089.5588 | 528.0699 | 5002.7443 | 2698.6643 | 601.8726 | 2596.053 | 714.2246 | 845.8536
2019-07-09 |  | 62.9599 | 620.9749 | 15.8906 | 0 | 1328.5824 | 25.6518 | 148.1168 | 393.3464 | 21.4692 | 5.6648e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365.9566 | 182.9612 | 48.4402 | 24.2178 | 191.1056 | 95.5439 | 0 | 93.5924 | 0 | 12.3686 | 5.9706 | 18.0831 | 11.9123 | 5.9556 | 0.66669 | 237.519 | 1072.5637 | 3034.9259 | 528.0699 | 5002.7443 | 2689.7038 | 608.6582 | 2688.18 | 583.0092 | 814.882
2019-07-10 |  | 63.2102 | 621.2228 | 15.9115 | 0 | 1351.1085 | 25.6447 | 148.1845 | 393.5209 | 21.5193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364.2805 | 182.1654 | 48.0984 | 24.0525 | 191.8661 | 95.9463 | 0 | 93.5926 | 0 | 12.3735 | 5.9727 | 18.2091 | 11.9999 | 6.0008 | 0.66664 | 244.1204 | 1076.4447 | 2915.268 | 528.0699 | 5002.7443 | 2696.536 | 614.5915 | 2646.3659 | 556.4262 | 789.8846
2019-07-11 |  | 63.1915 | 624.406 | 15.9438 | 0 | 1389.0232 | 26.2403 | 193.7045 | 542.3696 | 29.6884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457.9742 | 166.4887 | 65.8583 | 23.9417 | 267.7575 | 97.3387 | 0 | 116.7512 | 0 | 17.0547 | 5.9775 | 22.057 | 16.0048 | 5.8183 | 0.73339 | 251.4466 | 1080.2027 | 3038.3253 | 528.0699 | 5002.7443 | 2724.2901 | 622.4629 | 2972.1966 | 717.8654 | 941.5611
2019-07-12 |  | 62.9478 | 625.2532 | 15.9668 | 0 | 1450.4234 | 26.164 | 197.0937 | 553.2605 | 30.2955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418.3691 | 147.6382 | 69.6071 | 24.5636 | 274.1645 | 96.7499 | 0 | 118.8457 | 0 | 17.3968 | 5.9742 | 23.1355 | 16.9142 | 5.9688 | 0.73916 | 240.238 | 1085.7926 | 3152.4617 | 528.0699 | 5002.7443 | 2648.8679 | 630.9784 | 2964.574 | 554.8883 | 953.2493
2019-07-13 |  | 62.6184 | 624.6877 | 15.9146 | 0 | 1479.3394 | 26.1428 | 197.0291 | 553.1391 | 30.2939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414.5356 | 146.3258 | 67.507 | 23.8291 | 271.9332 | 95.989 | 0 | 118.8414 | 0 | 17.3931 | 5.9691 | 23.2407 | 16.9999 | 6.0007 | 0.73911 | 241.6659 | 1078.4915 | 2996.2842 | 528.0699 | 5002.7443 | 2608.491 | 628.4087 | 3078.9393 | 568.6656 | 865.5603
2019-07-14 |  | 63.0343 | 625.0989 | 15.9512 | 0 | 1464.3834 | 26.2559 | 197.0822 | 553.1234 | 30.2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424.2773 | 149.7435 | 67.9127 | 23.969 | 272.214 | 96.0746 | 0 | 118.847 | 0 | 17.391 | 5.9727 | 23.2624 | 17.0003 | 6 | 0.73913 | 241.6543 | 1078.6945 | 3103.7162 | 528.0699 | 5002.7443 | 2590.8284 | 627.6392 | 3005.6165 | 718.5003 | 827.2801
2019-07-15 |  | 65.9512 | 653.3839 | 16.6775 | 0 | 1509.0439 | 27.4931 | 198.5454 | 557.3535 | 30.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 428.9303 | 152.3474 | 65.6751 | 23.3265 | 281.0194 | 99.8125 | 0 | 120.5266 | 0 | 17.5235 | 6.2434 | 22.6072 | 16.4944 | 5.8585 | 0.73791 | 244.8309 | 1077.658 | 2999.6613 | 528.0699 | 5002.7443 | 2653.5558 | 628.6728 | 2978.4956 | 647.9307 | 877.8347
2019-07-16 |  | 75.0327 | 727.6449 | 18.4653 | 0 | 1714.3552 | 30.4479 | 189.5267 | 555.6953 | 30.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421.2719 | 166.2742 | 68.0075 | 26.8423 | 295.5388 | 116.6478 | 0 | 123.7402 | 0 | 17.473 | 6.9524 | 23.5526 | 16.6248 | 6.5617 | 0.717 | 241.991 | 1074.4682 | 3068.3704 | 566.093 | 5002.7443 | 2693.2683 | 619.8151 | 3104.622 | 537.4088 | 967.6605
2019-07-17 |  | 73.5196 | 727.0844 | 18.4846 | 0 | 1661.0992 | 30.481 | 186.8851 | 556.3447 | 30.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405.7659 | 167.0959 | 65.1165 | 26.8152 | 269.6804 | 111.0554 | 0 | 124.2074 | 0 | 17.4921 | 6.947 | 24.0085 | 16.7737 | 6.9075 | 0.70831 | 231.0755 | 1079.6054 | 3041.1382 | 630.9854 | 4981.0897 | 2696.5337 | 629.2965 | 3112.0766 | 611.1992 | 943.2971
2019-07-18 |  | 73.3253 | 726.3969 | 18.4901 | 0 | 1504.1358 | 30.5326 | 187.0514 | 556.8428 | 30.5208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408.9237 | 168.3724 | 64.9097 | 26.7263 | 269.2349 | 110.8562 | 0 | 124.2039 | 0 | 17.5098 | 6.9401 | 24.168 | 16.8727 | 6.9473 | 0.70834 | 240.0337 | 1041.1716 | 3050.2608 | 434.7539 | 3806.1815 | 2622.735 | 626.1553 | 3075.1404 | 575.7838 | 943.7554
2019-07-19 |  | 73.6862 | 750.8861 | 18.5221 | 0 | 1499.4249 | 30.605 | 186.9471 | 556.6369 | 30.4356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406.3615 | 168.0899 | 64.7188 | 26.7707 | 277.8236 | 114.9207 | 0 | 124.2031 | 0 | 17.5036 | 6.9397 | 23.9023 | 16.6571 | 6.8901 | 0.70739 | 239.9881 | 1062.3709 | 3174.1013 | 650.145 | 3806.1815 | 2602.2123 | 640.1953 | 3146.0183 | 455.6729 | 924.7363
2019-07-20 |  | 73.8813 | 801.8188 | 18.6387 | 0 | 1673.0477 | 30.7648 | 186.909 | 556.5188 | 30.4788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404.6682 | 161.5068 | 64.4934 | 25.7399 | 277.2375 | 110.648 | 0 | 124.8434 | 0 | 17.4972 | 7.0043 | 23.389 | 16.4502 | 6.5654 | 0.71474 | 242.817 | 1070.7934 | 3041.7289 | 538.9927 | 3806.1815 | 2579.3356 | 626.2642 | 3180.7895 | 458.7565 | 793.8443
2019-07-21 |  | 73.7902 | 825.8479 | 18.4846 | 0 | 1657.8342 | 30.6105 | 186.6583 | 555.7471 | 30.3976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.0446 | 170.1264 | 66.7284 | 27.4843 | 283.1877 | 116.6404 | 0 | 124.7524 | 0 | 17.4736 | 6.9593 | 24.2329 | 16.9166 | 6.9677 | 0.70827 | 242.3293 | 1063.1043 | 2966.335 | 521.7016 | 3806.1815 | 2525.7929 | 629.3139 | 3096.5104 | 414.0743 | 747.7444
2019-07-22 |  | 73.2268 | 834.7729 | 18.4983 | 0 | 1664.8515 | 30.2918 | 186.7875 | 556.1822 | 30.4261 | 9.4414e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.9154 | 169.9976 | 67.2421 | 27.6836 | 283.1185 | 116.5601 | 0 | 124.2118 | 0 | 17.4881 | 6.9352 | 24.2305 | 16.9163 | 6.9644 | 0.70837 | 242.9222 | 1057.4701 | 2928.1153 | 521.7016 | 3806.1815 | 2560.6296 | 625.1156 | 3020.9472 | 417.8995 | 812.25
2019-07-23 |  | 73.4093 | 855.4994 | 18.4062 | 0 | 1690.0615 | 30.6095 | 186.8804 | 556.3397 | 30.3873 | 4.7207e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.3083 | 169.7451 | 66.4632 | 27.3625 | 283.7474 | 116.8173 | 0 | 124.2145 | 0 | 17.4913 | 6.9426 | 24.1508 | 16.8613 | 6.9417 | 0.70837 | 243.6033 | 1043.2408 | 3044.0846 | 521.7016 | 3806.1815 | 2557.5399 | 629.5528 | 3082.7302 | 423.5283 | 812.801
2019-07-24 |  | 73.5471 | 859.0941 | 18.7246 | 0 | 1795.322 | 30.5982 | 185.48 | 552.3321 | 30.2857 | 4.7207e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408.4244 | 168.9907 | 66.2728 | 27.4212 | 284.3082 | 117.636 | 0 | 124.2122 | 0 | 17.3668 | 6.9488 | 23.8685 | 16.7161 | 6.9165 | 0.70733 | 243.2217 | 1043.14 | 2984.8936 | 521.7016 | 3806.1815 | 2562.536 | 610.8673 | 3087.2802 | 434.1321 | 881.1829
2019-07-25 |  | 74.092 | 859.5473 | 18.4999 | 0 | 1732.9639 | 30.6318 | 185.4139 | 552.167 | 30.2692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.5005 | 170.2106 | 67.0136 | 27.585 | 287.8173 | 118.4752 | 0 | 124.21 | 0 | 17.3602 | 7.0799 | 24.1194 | 16.917 | 6.9636 | 0.7084 | 237.0503 | 1046.2952 | 3061.7179 | 521.7016 | 3806.1815 | 2543.1568 | 630.4214 | 3248.1295 | 427.0519 | 896.2668
2019-07-26 |  | 73.6564 | 859.4981 | 18.3074 | 0 | 1745.7137 | 30.6153 | 185.4475 | 552.1179 | 30.1948 | 9.4414e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.9323 | 170.0322 | 67.2414 | 27.6878 | 282.7836 | 116.4411 | 0 | 124.2142 | 0 | 17.3582 | 6.9803 | 24.1076 | 16.9056 | 6.9612 | 0.70833 | 237.0506 | 1043.5407 | 3073.7975 | 521.7016 | 3806.1815 | 2551.0618 | 632.3095 | 3184.414 | 433.2309 | 891.0082
2019-07-27 |  | 73.8434 | 859.8768 | 18.3229 | 0 | 1768.3438 | 30.5545 | 185.343 | 552.0646 | 30.2607 | 1.8883e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421.7443 | 174.4412 | 65.1235 | 26.9363 | 283.5298 | 117.2731 | 0 | 124.2116 | 0 | 17.3572 | 6.9553 | 23.5878 | 16.5276 | 6.8361 | 0.7074 | 234.6659 | 1047.5476 | 3089.4418 | 521.7016 | 3806.1815 | 2553.2629 | 628.079 | 3189.6476 | 423.7689 | 836.3418
2019-07-28 |  | 74.0882 | 871.1247 | 18.4902 | 0 | 1785.3441 | 30.6307 | 186.3945 | 554.9163 | 30.3111 | 4.7207e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 474.5557 | 188.7112 | 65.49 | 26.0427 | 302.666 | 120.3577 | 0 | 124.3386 | 0 | 17.4479 | 6.9483 | 23.3456 | 16.5176 | 6.5684 | 0.71548 | 235.4704 | 1043.3301 | 3064.6734 | 521.7016 | 3806.1815 | 2423.4694 | 626.8872 | 3194.1103 | 432.6491 | 777.9991
2019-07-29 |  | 73.9972 | 873.5823 | 18.6037 | 0 | 1865.9784 | 30.4833 | 200.8789 | 598.2818 | 32.7555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 521.1694 | 197.7444 | 72.7453 | 27.6013 | 336.3089 | 127.6038 | 0 | 130.6774 | 0 | 18.8137 | 6.9553 | 25.5216 | 18.3137 | 6.9487 | 0.72494 | 239.2683 | 1046.0697 | 3034.2362 | 521.7016 | 3806.1815 | 2371.4592 | 630.4708 | 3365.8472 | 456.1106 | 872.0687
2019-07-30 |  | 77.3194 | 917.7376 | 19.5551 | 0 | 2024.4885 | 32.1129 | 239.1695 | 712.188 | 39.0502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 625.2158 | 208.969 | 85.928 | 28.7202 | 413.0939 | 138.0704 | 0 | 150.9103 | 0 | 22.3927 | 7.3071 | 29.5083 | 21.9079 | 7.3224 | 0.74949 | 239.1773 | 1044.1542 | 3091.1598 | 521.7016 | 3806.1815 | 2411.0008 | 632.9649 | 3838.4741 | 575.163 | 923.3712
2019-07-31 |  | 88.4648 | 1054.1608 | 22.1093 | 0 | 2042.5008 | 36.6951 | 245.4336 | 730.629 | 40.0852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 636.3924 | 228.019 | 89.2942 | 31.994 | 432.7514 | 155.0545 | 0 | 159.2008 | 0 | 22.9754 | 8.3561 | 30.7415 | 22.4443 | 8.0418 | 0.73621 | 239.7409 | 1042.6976 | 3054.8271 | 521.7016 | 3806.1815 | 2438.8606 | 640.7942 | 3965.1474 | 546.8138 | 922.9541
Monthly Chemical/Power Usage | 0 | 2058.254 | 21634.2145 | 518.0246 | 0 | 47610.8433 | 853.5025 | 5239.9612 | 15220.3811 | 832.9886 | 0.00069866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12184.292 | 5115.2721 | 1828.4025 | 763.3991 | 7720.2098 | 3214.1742 | 0 | 3425.047 | 0 | Total MG | Total MG | Total MG | Total MG | Total MG | Overall Ratio | 7258.2102 | 32035.4223 | 91065.5253 | 16030.2503 | 134505.3576 | 78239.6966 | 18528.0458 | 89399.5167 | 16023.2617 | 25385.1096
Cost per Gallon or lb or kW*Hr | 0.82128 | 1.4864 | 3.0825 | 4.3368 | 0 | 0.059975 | 3.739 | 0.82128 | 1.4864 | 4.3368 | 0 | 0 | 0 | 15.77 | 15.77 | 15.77 | 15.77 | 1.4864 | 1.4864 | 0.2996 | 0.2996 | 0.74349 | 0.74349 | 3.0825 | 3.0825 | 0 | 0.2996 | 0.82128 | 501.5221 | 203.0353 | 659.7032 | 459.9381 | 192.0275 | 0.70546 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065
Cost Per Month | 0 | 3059.2956 | 66686.6875 | 2246.5691 | 0 | 2855.4603 | 3191.2718 | 4303.4963 | 22622.8865 | 3612.5049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3650.4139 | 1532.5355 | 1359.4069 | 567.5829 | 23797.2689 | 9907.5763 | 0 | 1026.1441 | 0 | [6 empty] | 471.7837 | 2082.3024 | 5919.2591 | 1041.9663 | 8742.8482 | 5085.5803 | 1204.323 | 5810.9686 | 1041.512 | 1650.0321
2019-07-02 | [33 empty] | Natural Gas | 414.74 | NA | 535.49 | 324.65 | 486.19 | 2110.49 | 279.33 | NA | 38.34 | 117.08
Total Binney WPF Costs |  |  | South Platte Costs |  |  | Aurora Reservoir Costs |  |  | Labor Costs | [7 empty] | Monthly Truck Loads
Chemical | 150419.1006 |  | Chemical | 90046.9791 |  | Chemical | 59345.9774 |  | Monthly | 147210.66 | [6 empty] | Chemical |  | Gallon/Lbs | Loads
Electrical | 33050.5757 |  | Electrical | 18833.6554 |  | Electrical | 14216.9203 | [9 empty] | Ammonia |  | 2591.8017 | 0.71652
Natural Gas | 4306.31 |  | Natural Gas | 1657.6896 |  | Natural Gas | 2648.6204 |  | Material Costs | [7 empty] | Anionic Polymer |  | 0 | 0
Labor | 147210.66 |  | Labor | 73605.33 |  | Labor | 73605.33 |  | Monthly | 64269.67 | [6 empty] | Carbon Dioxide |  | 47610.8433 | 1.1903
Materials | 64269.67 |  | Materials | 32134.835 |  | Materials | 32134.835 | [9 empty] | Carbon PAC |  | 0.00069866 | 0.00069823
Binney MG Produced | 659.7032 |  | Net South Platte MG Produced | 192.0275 | 468.9274 | Net Aurora Reservoir MG Produced | 459.9381 | 129.0304 | [8 empty] | Cationic Polymer |  | 1351.0132 | 0.2604
Total Treated (MG) | 704.5573 |  | RWSP to Process (MG) | 203.0353 |  | RWAR to Process (MG) | 501.5221
Binney Cost per MG | 566.6768 |  | South Platte Cost per MG | 1065.2261 |  | Aurora Reservoir Cost per MG | 362.799 | [9 empty] | Chlorine |  | 20724.6111 | 1.2953
Binney Cost per KG | 0.56668 |  | South Platte Cost per KG | 1.0652 |  | Aurora Reservoir Cost per KG | 0.3628 | [9 empty] | Ferric Chloride |  | 17278.6351 | 4.4832
[17 empty] | Hydrogen Peroxide |  | 853.5025 | 0.17954
Notes: | [16 empty] | Potassium Permanganate |  | 5239.9612 | 0.40881
1. The difference between the "Binney MG Produced" and the Net numbers is the ammont of water needed from distribution to create the finished water (W3 to Chlorine and NaOH Motive) | [16 empty] | Sodium Hydroxide |  | 32568.5986 | 9.2955
Note on B40: Peter Bong: 3% Solution Strength
Note on C40: Peter Bong: 40% Solution Strength
Note on D40: Peter Bong: 50% Solution Strength
Note on E40: Peter Bong: 100% Solution Strength, PEC Cost
Note on F40: Peter Bong: 0.5% Solution Strength
Note on G40: Peter Bong: 99% Solution Strength
Note on H40: Peter Bong: 35% Solution Strength
Note on I40: Peter Bong: 3% Solution Strength
Note on J40: Peter Bong: 40% Solution Strength
Note on K40: Peter Bong: 100% Solution Strength
Note on L40: Peter Bong: 5.5% Solution Strength
Note on M40: Peter Bong: 0.5% Solution Strength
Note on N40: Peter Bong: 0.5% Solution Strength
Note on O40: Peter Bong: 100% Solution Strength
Note on P40: Peter Bong: 100% Solution Strength
Note on Q40: Peter Bong: 100% Solution Strength
Note on R40: Peter Bong: 100% Solution Strength
Note on S40: Peter Bong: 40% Solution Strength
Note on T40: Peter Bong: 40% Solution Strength
Note on U40: Peter Bong: 100% Solution Strength
Note on V40: Peter Bong: 100% Solution Strength
Note on Y40: Peter Bong: 50% Solution Strength
Note on Z40: Peter Bong: 50% Solution Strength
Note on AB40: Peter Bong: 100% Solution Strength
Note on AC40: Peter Bong: 3% Solution Strength
Note on AJ40: Peter Bong: Cost per kW*Hr
Note on AK40: Peter Bong: Cost per kW*Hr
Note on AL40: Peter Bong: Cost per kW*Hr
Note on AM40: Peter Bong: Cost per kW*Hr
Note on AN40: Peter Bong: Cost per kW*Hr
Note on AO40: Peter Bong: Cost per kW*Hr
Note on AP40: Peter Bong: Cost per kW*Hr
Note on AQ40: Peter Bong: Cost per kW*Hr
Note on AR40: Peter Bong: Cost per kW*Hr
Note on AS40: Peter Bong: Cost per kW*Hr
Note on AI42: Peter Bong: See Utility Summary Seet For Data

## AUGUST
Current Application Point |  | Notes: Chemical are arranged in general process flow
Not in Use
| South Platte | [6 empty] | Aurora Reservoir | [5 empty] | Filters/Adsorbers | [5 empty] | Finished Water | [6 empty] | From Chlorinator 5 | Valve Vault 1 (To Wemlinger RWAR) | RWAR Flow to Process | RWSP Flow to Process | Finished Water Flow | AR Net to Distribution | SP Net to Distribution | AR to Total Flow Blend | Blended&RW | Softening | Pre-Chem | Floc/Sed | UV/AOP | Filtration/Ad | Post-Chem | Finished | Recycle | Control | pass | bwpfyearly
| KMnO4 (RW) | FeCl3 (Rapid Mix & Flow Split) | NaOH (Rapid Mix) | PEC/PEA (Reactors) | PEA (Sludge) | CO2 (Post Softening) | H202 (UV) | KMnO4 (RW) | FeCl3 (Rapid Mix) | PEC (Rapid Mix) | PAC (Basin 1 & 2) | PEA (Basin 1 & 2) | PEA (Sludge) | PEN AR (FIC) | PEN SP (FIC) | PEN AR (Individual Filters) | PEN SP (Individual Filters) | FeCl3 AR (Backwash Supply) | FeCl3 SP (Backwash Supply) | Cl2 AR | Cl2 SP | NH3 AR (CCB Effluent) | NH3 SP (CCB Effluent) | NaOH AR (CCB Effluent) | NaOH SP (CCB Effluent) | Fluoride(CCB Effluent) | Cl2 to RWAR, RWSP, ARFIC, or SPFIC | KMnO4 (RWAR to Wemlinger) |  |  | Total Produced From Binney
| Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Gallons per Day | MGD | MGD | MGD | MGD | MGD | Ratio | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day
2019-08-01 |  | 94.9481 | 1137.4042 | 23.7536 | 0 | 1742.2876 | 37.6769 | 250.0836 | 744.6625 | 40.7867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 644.6623 | 252.2306 | 93.3948 | 36.5416 | 442.4434 | 173.1104 | 0 | 164.7099 | 0 | 23.4133 | 8.9628 | 31.9402 | 22.7043 | 8.8833 | 0.71877 | 240.8911 | 1050.576 | 3064.3997 | 521.7016 | 3806.1815 | 2632.7609 | 644.1036 | 4180.8396 | 479.7182 | 874.6314
2019-08-02 |  | 94.8112 | 1136.3549 | 23.6095 | 0 | 1708.2914 | 36.0451 | 250.2872 | 745.1199 | 40.8118 | 5.6648e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 627.3776 | 246.6404 | 90.5448 | 35.5958 | 438.9943 | 172.5814 | 0 | 164.7391 | 0 | 23.4276 | 8.9551 | 31.7159 | 22.5378 | 8.8603 | 0.71781 | 248.8107 | 1045.9757 | 3034.1875 | 521.7016 | 3806.1815 | 2660.842 | 640.4762 | 4128.8182 | 435.1403 | 814.036
2019-08-03 |  | 94.9022 | 1136.0865 | 23.8602 | 0 | 1818.5711 | 35.9936 | 250.1716 | 744.7518 | 40.8234 | 2.8324e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640.0683 | 248.5554 | 92.3643 | 35.8675 | 446.2625 | 173.2955 | 0 | 164.7322 | 0 | 23.4175 | 8.9535 | 32.2384 | 22.9999 | 8.9315 | 0.72029 | 248.9349 | 1050.4401 | 3080.5976 | 521.7016 | 3806.1815 | 2592.0778 | 634.7921 | 4227.1233 | 477.3743 | 863.3628
2019-08-04 |  | 94.9099 | 1137.7118 | 23.6117 | 0 | 1923.8162 | 36.0955 | 249.9269 | 744.0686 | 40.7491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 636.2077 | 248.9537 | 91.4043 | 35.7673 | 427.9879 | 167.4755 | 0 | 165.0896 | 0 | 23.396 | 8.9665 | 32.1119 | 22.8543 | 8.9431 | 0.71875 | 248.9349 | 1053.191 | 3009.1718 | 521.7016 | 3806.1815 | 2589.8284 | 640.5469 | 4271.5671 | 509.9159 | 821.4498
2019-08-05 |  | 94.4247 | 1133.6908 | 23.5933 | 0 | 1918.3271 | 36.0402 | 249.9572 | 744.3633 | 40.7998 | 3.7766e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622.0095 | 235.0939 | 91.3253 | 34.5172 | 423.3122 | 159.9945 | 0 | 163.0567 | 0 | 23.4014 | 8.9335 | 31.2577 | 22.4596 | 8.4888 | 0.72571 | 248.9349 | 1039.7166 | 3071.3538 | 521.7016 | 3806.1815 | 2625.5462 | 635.7061 | 4148.8459 | 494.3503 | 869.0811
2019-08-06 |  | 94.9863 | 1138.7692 | 24.5546 | 0 | 1863.3979 | 36.1263 | 251.1413 | 747.7855 | 41.0105 | 0.00022659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571.2209 | 204.0989 | 95.3403 | 34.0654 | 435.5808 | 155.6343 | 0 | 160.6773 | 0 | 23.5097 | 8.974 | 30.5834 | 22.233 | 7.9439 | 0.73676 | 248.9349 | 1035.4777 | 3054.8076 | 521.7016 | 3806.1815 | 2633.3657 | 633.3178 | 4045.5765 | 445.5148 | 872.4774
2019-08-07 |  | 98.4677 | 1187.4717 | 24.8788 | 0 | 2102.6469 | 37.5729 | 248.4868 | 739.8361 | 40.5189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520.4364 | 210.7475 | 91.7402 | 37.1496 | 426.9576 | 172.8938 | 0 | 160.2092 | 0 | 23.2648 | 9.3576 | 32.0911 | 22.5214 | 9.1199 | 0.71177 | 238.9211 | 1033.4197 | 3052.1757 | 521.7016 | 3806.1815 | 2630.3386 | 638.9897 | 4186.9186 | 495.8905 | 869.546
2019-08-08 |  | 100.2472 | 1201.8591 | 25.2996 | 0 | 2161.4659 | 37.9653 | 267.226 | 764.6187 | 41.8496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 527.0994 | 205.3154 | 93.0326 | 36.238 | 419.7555 | 163.5028 | 0 | 163.0106 | 0 | 24.0403 | 9.4711 | 32.4852 | 23.0382 | 8.9738 | 0.71967 | 236.28 | 1012.999 | 2950.2068 | 521.7016 | 3806.1815 | 2630.4702 | 633.9245 | 4448.2047 | 475.5011 | 868.8869
2019-08-09 |  | 99.8265 | 1197.9406 | 24.9766 | 0 | 2266.013 | 37.9351 | 280.3533 | 765.1857 | 41.9447 | 4.7207e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 528.5878 | 206.0169 | 93.0009 | 36.2471 | 421.3813 | 164.2332 | 0 | 162.5052 | 0 | 24.0596 | 9.4397 | 32.6071 | 23.1164 | 9.0096 | 0.71955 | 240.0733 | 1014.9759 | 3036.2779 | 521.7016 | 3806.1815 | 2623.7724 | 617.6989 | 4377.7908 | 482.2554 | 853.7879
2019-08-10 |  | 99.9951 | 1197.1873 | 25.4134 | 0 | 2150.2256 | 37.9475 | 280.5368 | 765.7574 | 41.9361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 528.3443 | 214.5215 | 92.383 | 37.5099 | 420.9966 | 170.9355 | 0 | 162.772 | 0 | 24.0766 | 9.4344 | 33.0042 | 23.1283 | 9.3907 | 0.71122 | 245.9164 | 1015.2674 | 3018.1121 | 521.7016 | 3806.1815 | 2606.6717 | 614.4902 | 4367.362 | 474.794 | 798.0304
2019-08-11 |  | 99.5753 | 1197.8438 | 25.4188 | 0 | 1980.8104 | 37.9912 | 280.182 | 764.6863 | 41.9232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 533.5984 | 215.72 | 93.7343 | 37.8943 | 429.0342 | 173.4474 | 0 | 162.7658 | 0 | 24.0469 | 9.4388 | 33.2865 | 23.3667 | 9.4465 | 0.71211 | 243.3345 | 1012.4658 | 2987.5059 | 498.627 | 5144.0014 | 2594.1774 | 605.5883 | 4353.0165 | 432.3847 | 770.0211
2019-08-12 |  | 99.3634 | 1198.8488 | 25.1904 | 0 | 1836.8678 | 37.9073 | 279.9892 | 764.1765 | 41.8466 | 1.8883e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 546.0708 | 215.7769 | 92.5298 | 36.5627 | 417.3427 | 164.9107 | 0 | 162.6973 | 0 | 24.0268 | 9.4468 | 32.403 | 22.9141 | 9.0544 | 0.71677 | 244.033 | 1017.5775 | 3039.2206 | 465.3241 | 7179.9807 | 2611.8763 | 601.5971 | 4285.1704 | 425.9992 | 791.0967
2019-08-13 |  | 98.9321 | 1196.0757 | 25.1671 | 0 | 1881.8622 | 37.7676 | 279.4175 | 762.7813 | 41.7686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.8767 | 233.2355 | 95.2753 | 38.5205 | 427.5989 | 172.8814 | 0 | 162.7692 | 0 | 23.9811 | 9.425 | 33.4037 | 23.4981 | 9.5005 | 0.71209 | 238.1182 | 1020.2141 | 3039.5935 | 465.3241 | 7179.9807 | 2602.7631 | 607.9503 | 4482.1602 | 434.4345 | 869.4985
2019-08-14 |  | 99.6355 | 1196.3981 | 25.6066 | 0 | 1975.1684 | 37.8555 | 279.4855 | 762.7545 | 41.8166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561.3585 | 218.8952 | 93.5411 | 36.4753 | 416.9496 | 162.5846 | 0 | 162.8159 | 0 | 23.9849 | 9.4289 | 32.2308 | 22.8986 | 8.929 | 0.71946 | 239.9141 | 1022.8824 | 3027.1898 | 465.3241 | 7179.9807 | 2627.3053 | 612.304 | 4306.6917 | 431.9177 | 825.1171
2019-08-15 |  | 102.6595 | 1195.3534 | 25.4085 | 0 | 2035.486 | 37.7983 | 286.6016 | 851.903 | 46.7962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618.1865 | 223.8821 | 104.9962 | 38.0254 | 484.3429 | 175.4094 | 0 | 176.1168 | 0 | 26.8263 | 9.42 | 35.864 | 26.0022 | 9.4169 | 0.73413 | 238.8578 | 1025.0721 | 3218.4917 | 465.3241 | 7179.9807 | 2649.479 | 613.3253 | 4742.4054 | 434.9213 | 872.6668
2019-08-16 |  | 99.9408 | 1195.3424 | 24.5692 | 0 | 1996.4027 | 37.8381 | 303.9205 | 988.8826 | 54.3397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 688.3102 | 215.8283 | 120.3369 | 37.7332 | 606.1239 | 190.0577 | 0 | 197.6101 | 0 | 31.0934 | 9.4196 | 39.2753 | 29.5781 | 9.2746 | 0.76129 | 234.7863 | 1018.9228 | 3087.7666 | 465.3241 | 7179.9807 | 2613.6991 | 620.55 | 5414.49 | 430.1725 | 833.9552
2019-08-17 |  | 99.9249 | 1196.1258 | 25.1945 | 0 | 2036.9673 | 37.8736 | 285.8363 | 1003.1392 | 55.1121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 696.625 | 200.2829 | 124.1955 | 35.7068 | 642.0786 | 184.6006 | 0 | 200.4493 | 0 | 31.5388 | 9.4256 | 39.2917 | 30.2193 | 8.6882 | 0.7767 | 244.8491 | 1024.0039 | 3028.8168 | 465.3241 | 7179.9807 | 2583.7063 | 609.6368 | 5567.8205 | 445.32 | 826.0772
2019-08-18 |  | 99.8109 | 1195.1794 | 25.3401 | 0 | 2141.7881 | 37.9148 | 266.6227 | 935.5261 | 51.318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637.5816 | 209.0114 | 114.9076 | 37.6689 | 609.9662 | 199.9585 | 0 | 189.2035 | 0 | 29.4132 | 9.4185 | 38.863 | 28.982 | 9.5009 | 0.75311 | 247.8069 | 1021.5817 | 2939.5783 | 465.3241 | 7179.9807 | 2586.5652 | 604.339 | 5303.2781 | 458.7988 | 736.2352
2019-08-19 |  | 99.3974 | 1196.046 | 25.3893 | 0 | 1976.0179 | 37.9058 | 298.2446 | 1011.9085 | 55.6182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 683.489 | 196.3484 | 126.4584 | 36.3282 | 649.5284 | 186.5925 | 0 | 201.4126 | 0 | 31.8148 | 9.425 | 40.2546 | 30.9871 | 8.9018 | 0.77684 | 233.9451 | 1030.3822 | 2831.2959 | 465.3241 | 7179.9807 | 2586.3329 | 622.9275 | 5603.6736 | 473.7086 | 914.4569
2019-08-20 |  | 99.7457 | 1195.1829 | 25.4113 | 0 | 1948.5228 | 37.8058 | 289.1803 | 971.1503 | 53.3437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660.6209 | 208.4432 | 123.6843 | 39.0256 | 630.6807 | 198.9963 | 0 | 195.0758 | 0 | 30.5331 | 9.4188 | 39.7771 | 29.9285 | 9.4432 | 0.76015 | 230.793 | 1032.44 | 3044.4203 | 465.3241 | 7179.9807 | 2611.1996 | 633.1556 | 5771.7374 | 501.069 | 914.8118
2019-08-21 |  | 99.2805 | 1195.1552 | 25.3334 | 0 | 1906.6323 | 37.8148 | 291.3417 | 878.8313 | 48.2971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619.1391 | 217.2243 | 112.7329 | 39.5522 | 545.7235 | 191.4665 | 0 | 180.5551 | 0 | 27.652 | 9.4189 | 36.7927 | 26.9834 | 9.4671 | 0.74028 | 234.6729 | 1029.8574 | 3055.4375 | 465.3241 | 7179.9807 | 2602.4816 | 626.2021 | 4844.4999 | 447.1424 | 841.1964
2019-08-22 |  | 100.3882 | 1200.0033 | 25.2418 | 0 | 1917.0719 | 37.7727 | 296.9324 | 828.4289 | 45.4629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 567.7943 | 203.3725 | 103.3548 | 37.0196 | 511.3737 | 183.1638 | 0 | 172.4612 | 0 | 26.0445 | 9.418 | 34.6589 | 25.2741 | 9.0527 | 0.73628 | 239.1248 | 1031.3971 | 3118.3483 | 465.3241 | 7179.9807 | 2600.7313 | 578.9303 | 4605.0463 | 435.9116 | 880.0534
2019-08-23 |  | 100.1045 | 1207.6048 | 25.2092 | 0 | 2032.2487 | 37.862 | 326.6722 | 891.7565 | 48.9595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 599.3282 | 206.6814 | 111.193 | 38.3455 | 537.371 | 185.3151 | 0 | 182.3326 | 0 | 28.042 | 9.4187 | 36.9732 | 27.2392 | 9.3936 | 0.74357 | 238.0941 | 1027.5124 | 3013.8307 | 465.3241 | 7179.9807 | 2606.9997 | 539.0854 | 4891.5296 | 436.6666 | 843.1851
2019-08-24 |  | 99.9806 | 1207.5931 | 25.212 | 0 | 2045.1911 | 37.7828 | 347.2209 | 980.2808 | 53.8773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 658.9406 | 203.8059 | 124.8133 | 38.6039 | 618.0337 | 191.1537 | 0 | 196.3649 | 0 | 30.8217 | 9.4192 | 39.8228 | 30.1069 | 9.3119 | 0.76377 | 241.0438 | 1030.4417 | 2965.8636 | 465.3241 | 7179.9807 | 2561.0175 | 512.4264 | 5416.9453 | 426.0796 | 734.772
2019-08-25 |  | 99.8589 | 1209.3601 | 25.1739 | 0 | 2065.7549 | 37.9025 | 332.2615 | 939.8287 | 51.6336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 624.7779 | 197.3789 | 116.7777 | 36.8922 | 609.658 | 192.6022 | 0 | 189.828 | 0 | 29.5484 | 9.4323 | 38.027 | 28.5317 | 9.0137 | 0.75993 | 242.8383 | 1031.7274 | 2975.7887 | 465.3241 | 7179.9807 | 2577.4663 | 512.9134 | 5252.2976 | 460.8003 | 815.0993
2019-08-26 |  | 99.8761 | 1205.5202 | 24.9696 | 0 | 2058.4577 | 37.7533 | 329.8136 | 925.9105 | 50.8187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622.368 | 206.7309 | 116.6134 | 38.7353 | 602.8456 | 200.2461 | 0 | 187.2245 | 0 | 29.1126 | 9.4031 | 38.5664 | 28.5996 | 9.4999 | 0.75066 | 233.8451 | 1027.0483 | 2874.5503 | 465.3241 | 7179.9807 | 2579.3355 | 517.6706 | 5089.482 | 482.0518 | 776.0121
2019-08-27 |  | 99.9974 | 1207.2006 | 25.0425 | 0 | 1967.2266 | 37.8211 | 290.4866 | 815.3369 | 44.7056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535.163 | 200.9993 | 99.1373 | 37.2345 | 522.2143 | 196.136 | 0 | 170.6043 | 0 | 25.6351 | 9.4147 | 34.5487 | 24.7896 | 9.3106 | 0.72696 | 239.0729 | 1030.6742 | 2945.94 | 465.3241 | 7179.9807 | 2590.0955 | 501.9464 | 4517.8921 | 438.1381 | 775.4101
2019-08-28 |  | 99.3193 | 1207.4079 | 25.6669 | 0 | 1860.5933 | 37.7965 | 304.788 | 844.2422 | 46.2905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 559.4116 | 198.3072 | 101.4372 | 35.9587 | 517.7106 | 183.5245 | 0 | 174.8939 | 0 | 26.5447 | 9.4178 | 34.6018 | 25.2296 | 8.9437 | 0.73828 | 239.8546 | 1027.4223 | 3013.0756 | 465.3241 | 7179.9807 | 2590.8271 | 505.0014 | 4613.547 | 407.0687 | 853.2902
2019-08-29 |  | 99.9081 | 1206.9438 | 25.1336 | 0 | 2010.9657 | 37.8225 | 281.147 | 819.0207 | 44.9204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550.1122 | 206.8605 | 99.1431 | 37.2811 | 529.0272 | 198.9319 | 0 | 171.4968 | 0 | 25.7483 | 9.4132 | 34.8543 | 25.0126 | 9.4056 | 0.72673 | 238.8102 | 1032.8305 | 3108.9768 | 465.3241 | 7179.9807 | 2647.2272 | 522.5372 | 4772.1512 | 431.9349 | 920.7719
2019-08-30 |  | 99.9343 | 1208.2727 | 25.2161 | 0 | 2187.9722 | 37.8567 | 230.9082 | 661.6867 | 36.1549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455.6811 | 204.8411 | 75.4974 | 33.9381 | 412.402 | 185.386 | 0 | 146.7406 | 0 | 20.8014 | 9.4241 | 29.06 | 19.7693 | 8.8868 | 0.68988 | 237.0985 | 1029.7175 | 2984.5236 | 465.3241 | 7179.9807 | 2661.7086 | 520.346 | 3886.7225 | 447.9324 | 864.4551
2019-08-31 |  | 99.6994 | 1207.0305 | 25.5171 | 0 | 2211.6026 | 37.7759 | 179.9918 | 504.9957 | 27.5411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367.6961 | 225.415 | 60.6058 | 37.1542 | 284.2734 | 174.273 | 0 | 122.2528 | 0 | 15.8816 | 9.4145 | 24.8577 | 15.2534 | 9.3511 | 0.61994 | 242.2482 | 1031.2304 | 3057.205 | 465.3241 | 7179.9807 | 2645.929 | 524.4675 | 3278.6636 | 458.4902 | 801.5048
Monthly Chemical/Power Usage | 0 | 3064.8517 | 36828.9646 | 773.9631 | 0 | 61728.6531 | 1164.0171 | 8639.2148 | 25413.377 | 1393.7751 | 0.00041542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18209.1441 | 6681.2151 | 3135.496 | 1144.1556 | 15307.9512 | 5565.2948 | 0 | 5337.1726 | 0 | Total MG | Total MG | Total MG | Total MG | Total MG | Overall Ratio | 7469.7733 | 31907.4406 | 93728.7102 | 15022.1239 | 186805.4309 | 80956.5974 | 18326.9467 | 143382.2678 | 14111.3977 | 25964.9766
Cost per Gallon or lb or kW*Hr | 0.82128 | 1.4864 | 3.0825 | 4.3368 | 0 | 0.059975 | 3.739 | 0.82128 | 1.4864 | 4.3368 | 0 | 0 | 0 | 15.77 | 15.77 | 15.77 | 15.77 | 1.4864 | 1.4864 | 0.2996 | 0.2996 | 0.74349 | 0.74349 | 3.0825 | 3.0825 | 0 | 0.2996 | 0.82128 | 799.0986 | 289.3096 | 1067.4481 | 772.7573 | 282.3374 | 0.73241 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065
Cost Per Month | 0 | 4555.457 | 113523.9576 | 3356.5231 | 0 | 3702.176 | 4352.2954 | 7095.2489 | 37773.2948 | 6044.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5455.4596 | 2001.692 | 2331.2235 | 850.6732 | 47186.2086 | 17154.8209 | 0 | 1599.0169 | 0 | [6 empty] | 485.5353 | 2073.9836 | 6092.3662 | 976.4381 | 12142.353 | 5262.1788 | 1191.2515 | 9319.8474 | 917.2409 | 1687.7235
2019-08-02 | [33 empty] | Natural Gas | 201.26 | NA | 78.29 | 37.78 | 199.37 | 915.42 | 87.04 | NA | 37.78 | 59.43
Total Binney WPF Costs |  |  | South Platte Costs |  |  | Aurora Reservoir Costs |  |  | Labor Costs | [7 empty] | Monthly Truck Loads
Chemical | 256982.5714 |  | Chemical | 149497.5952 |  | Chemical | 105885.9593 |  | Monthly | 224193.7 | [6 empty] | Chemical |  | Gallon/Lbs | Loads
Electrical | 40148.9182 |  | Electrical | 22915.7688 |  | Electrical | 17233.1494 | [9 empty] | Ammonia |  | 4279.6516 | 1.1831
Natural Gas | 1616.37 |  | Natural Gas | 609.2287 |  | Natural Gas | 1007.1413 |  | Material Costs | [7 empty] | Anionic Polymer |  | 0 | 0
Labor | 224193.7 |  | Labor | 112096.85 |  | Labor | 112096.85 |  | Monthly | 179847.95 | [6 empty] | Carbon Dioxide |  | 61728.6531 | 1.5432
Materials | 179847.95 |  | Materials | 89923.975 |  | Materials | 89923.975 | [9 empty] | Carbon PAC |  | 0.00041542 | 0.00041516
Binney MG Produced | 1067.4481 |  | Net South Platte MG Produced | 282.3374 |  | Net Aurora Reservoir MG Produced | 772.7573 | [9 empty] | Cationic Polymer |  | 2167.7382 | 0.41782
Total Treated (MG) | 1088.4083 |  | RWSP to Process (MG) | 289.3096 |  | RWAR to Process (MG) | 799.0986
Binney Cost per MG | 645.7039 |  | South Platte Cost per MG | 1296.3392 |  | Aurora Reservoir Cost per MG | 408.1437 | [9 empty] | Chlorine |  | 30227.5318 | 1.8892
Binney Cost per KG | 0.6457 |  | South Platte Cost per KG | 1.2963 | 529.4998 | Aurora Reservoir Cost per KG | 0.40814 | 137.0236 | [8 empty] | Ferric Chloride |  | 28478.2286 | 7.3892
[17 empty] | Hydrogen Peroxide |  | 1164.0171 | 0.24485
Notes: | [16 empty] | Potassium Permanganate |  | 8639.2148 | 0.674
1. The difference between the "Binney MG Produced" and the Net numbers is the ammont of water needed from distribution to create the finished water (W3 to Chlorine and NaOH Motive) | [16 empty] | Sodium Hydroxide |  | 57702.2107 | 16.469
Note on B40: Peter Bong: 3% Solution Strength
Note on C40: Peter Bong: 40% Solution Strength
Note on D40: Peter Bong: 50% Solution Strength
Note on E40: Peter Bong: 100% Solution Strength, PEC Cost
Note on F40: Peter Bong: 0.5% Solution Strength
Note on G40: Peter Bong: 99% Solution Strength
Note on H40: Peter Bong: 35% Solution Strength
Note on I40: Peter Bong: 3% Solution Strength
Note on J40: Peter Bong: 40% Solution Strength
Note on K40: Peter Bong: 100% Solution Strength
Note on L40: Peter Bong: 5.5% Solution Strength
Note on M40: Peter Bong: 0.5% Solution Strength
Note on N40: Peter Bong: 0.5% Solution Strength
Note on O40: Peter Bong: 100% Solution Strength
Note on P40: Peter Bong: 100% Solution Strength
Note on Q40: Peter Bong: 100% Solution Strength
Note on R40: Peter Bong: 100% Solution Strength
Note on S40: Peter Bong: 40% Solution Strength
Note on T40: Peter Bong: 40% Solution Strength
Note on U40: Peter Bong: 100% Solution Strength
Note on V40: Peter Bong: 100% Solution Strength
Note on Y40: Peter Bong: 50% Solution Strength
Note on Z40: Peter Bong: 50% Solution Strength
Note on AB40: Peter Bong: 100% Solution Strength
Note on AC40: Peter Bong: 3% Solution Strength
Note on AJ40: Peter Bong: Cost per kW*Hr
Note on AK40: Peter Bong: Cost per kW*Hr
Note on AL40: Peter Bong: Cost per kW*Hr
Note on AM40: Peter Bong: Cost per kW*Hr
Note on AN40: Peter Bong: Cost per kW*Hr
Note on AO40: Peter Bong: Cost per kW*Hr
Note on AP40: Peter Bong: Cost per kW*Hr
Note on AQ40: Peter Bong: Cost per kW*Hr
Note on AR40: Peter Bong: Cost per kW*Hr
Note on AS40: Peter Bong: Cost per kW*Hr
Note on AI42: Peter Bong: See Utility Summary Seet For Data

## SEPTEMBER
Current Application Point |  | Notes: Chemical are arranged in general process flow
Not in Use
[45 empty] | pass | bwpfcost
| South Platte | [6 empty] | Aurora Reservoir | [5 empty] | Filters/Adsorbers | [5 empty] | Finished Water | [6 empty] | From Chlorinator 5 | Valve Vault 1 (To Wemlinger RWAR) | RWAR Flow to Process | RWSP Flow to Process | Finished Water Flow | AR Net to Distribution | SP Net to Distribution | AR to Total Flow Blend | Blended&RW | Softening | Pre-Chem | Floc/Sed | UV/AOP | Filtration/Ad | Post-Chem | Finished | Recycle | Control
| KMnO4 (RW) | FeCl3 (Rapid Mix & Flow Split) | NaOH (Rapid Mix) | PEC/PEA (Reactors) | PEA (Sludge) | CO2 (Post Softening) | H202 (UV) | KMnO4 (RW) | FeCl3 (Rapid Mix) | PEC (Rapid Mix) | PAC (Basin 1 & 2) | PEA (Basin 1 & 2) | PEA (Sludge) | PEN AR (FIC) | PEN SP (FIC) | PEN AR (Individual Filters) | PEN SP (Individual Filters) | FeCl3 AR (Backwash Supply) | FeCl3 SP (Backwash Supply) | Cl2 AR | Cl2 SP | NH3 AR (CCB Effluent) | NH3 SP (CCB Effluent) | NaOH AR (CCB Effluent) | NaOH SP (CCB Effluent) | Fluoride(CCB Effluent) | Cl2 to RWAR, RWSP, ARFIC, or SPFIC | KMnO4 (RWAR to Wemlinger) |  |  | Total Produced From Binney
| Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Gallons per Day | MGD | MGD | MGD | MGD | MGD | Ratio | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day
2019-09-01 |  | 99.987 | 1205.7103 | 25.0846 | 0 | 2073.6037 | 37.7569 | 179.9875 | 504.9681 | 27.5713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373.8617 | 215.5569 | 62.1453 | 35.831 | 259.21 | 149.4524 | 0 | 121.6236 | 0 | 15.8847 | 9.4044 | 24.3363 | 15.2625 | 8.7999 | 0.63429 | 241.6171 | 1039.0577 | 3001.6674 | 465.3241 | 7179.9807 | 2644.45 | 547.921 | 3290.2937 | 478.444 | 861.5522
2019-09-02 |  | 98.9301 | 1206.1574 | 24.8299 | 0 | 2054.5474 | 37.8105 | 179.9957 | 505.078 | 27.4992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376.6289 | 230.868 | 62.8024 | 38.497 | 262.074 | 160.6475 | 0 | 120.2818 | 0 | 15.884 | 9.407 | 25.128 | 15.4123 | 9.4475 | 0.61997 | 239.3279 | 1043.0104 | 3146.3162 | 465.3241 | 7179.9807 | 2665.4097 | 558.4644 | 3296.2292 | 495.7129 | 887.6911
2019-09-03 |  | 99.5832 | 1206.8302 | 24.9398 | 0 | 2016.5838 | 37.8256 | 175.9579 | 505.0135 | 27.6144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375.7308 | 230.2982 | 62.3709 | 38.2292 | 261.86 | 160.5029 | 0 | 120.4473 | 0 | 15.8844 | 9.4129 | 25.0859 | 15.3715 | 9.4217 | 0.61999 | 232.5694 | 1041.1604 | 3030.2165 | 465.3241 | 7179.9807 | 2655.1157 | 544.4137 | 3288.2978 | 480.4443 | 885.1023
2019-09-04 |  | 99.8087 | 1207.8331 | 24.8928 | 0 | 2027.0157 | 37.8467 | 169.6809 | 505.1147 | 27.5657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373.9556 | 221.5278 | 61.0515 | 36.1664 | 262.6755 | 155.6065 | 0 | 121.8179 | 0 | 15.8852 | 9.4212 | 24.7899 | 15.4155 | 9.132 | 0.62799 | 237.7468 | 1047.196 | 2989.7284 | 465.3241 | 7179.9807 | 2654.3272 | 528.1396 | 3249.8277 | 468.5342 | 848.5779
2019-09-05 |  | 100.4244 | 1205.7727 | 24.8045 | 0 | 2007.3668 | 37.8498 | 178.2016 | 505.3174 | 27.5783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370.8115 | 227.3371 | 60.3667 | 37.0096 | 257.9886 | 158.1677 | 0 | 121.587 | 0 | 15.888 | 9.4051 | 24.6251 | 15.0935 | 9.2535 | 0.61993 | 234.7184 | 1044.3448 | 3027.578 | 465.3241 | 7179.9807 | 2811.3513 | 541.783 | 3277.5545 | 483.942 | 914.5334
2019-09-06 |  | 100.0938 | 1208.5982 | 25.0204 | 0 | 1923.9228 | 37.8161 | 192.4649 | 504.8481 | 27.5302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371.0125 | 219.1843 | 61.2384 | 36.178 | 260.5996 | 153.9553 | 0 | 121.5941 | 0 | 15.8732 | 9.4263 | 24.3835 | 15.1505 | 8.9505 | 0.62863 | 234.7184 | 1046.9116 | 2980.6747 | 465.3241 | 7179.9807 | 2661.3114 | 528.5119 | 3165.6994 | 467.8169 | 860.0281
2019-09-07 |  | 99.6257 | 1206.3664 | 25.2788 | 0 | 1913.1083 | 37.9363 | 198.7406 | 507.4773 | 27.6785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376.4011 | 230.6889 | 60.1872 | 36.8876 | 265.9655 | 163.0051 | 0 | 121.8369 | 0 | 15.9501 | 9.41 | 25.0858 | 15.3815 | 9.427 | 0.62001 | 243.4778 | 1040.3246 | 2965.172 | 465.3241 | 7179.9807 | 2635.7811 | 504.827 | 3296.7703 | 448.783 | 781.7726
2019-09-08 |  | 99.538 | 1206.3985 | 25.1961 | 0 | 1880.96 | 37.8907 | 195.1985 | 504.7115 | 27.5308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370.9409 | 219.4457 | 58.6978 | 34.7251 | 261.4807 | 154.6899 | 0 | 121.4784 | 0 | 15.8677 | 9.4099 | 24.3773 | 15.1394 | 8.9564 | 0.6283 | 244.4581 | 1043.9559 | 2938.2434 | 465.3241 | 7179.9807 | 2572.3088 | 502.5393 | 3188.8802 | 447.2415 | 689.0648
2019-09-09 |  | 99.853 | 1206.3405 | 25.3213 | 0 | 1825.711 | 37.8022 | 196.1427 | 505.2202 | 27.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376.9849 | 231.0395 | 59.6443 | 36.5537 | 266.4243 | 163.2811 | 0 | 121.2405 | 0 | 15.884 | 9.4096 | 25.1341 | 15.4142 | 9.4468 | 0.62002 | 232.1459 | 1029.9199 | 2992.6658 | 465.3241 | 7179.9807 | 2603.4503 | 480.6019 | 3253.3581 | 442.6441 | 748.3945
2019-09-10 |  | 95.7358 | 1159.9637 | 24.4013 | 0 | 1769.1856 | 36.4159 | 187.9316 | 436.1328 | 23.8565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330.6875 | 226.1943 | 49.9791 | 34.1863 | 227.7285 | 155.7691 | 0 | 109.8733 | 0 | 13.7074 | 9.047 | 22.3278 | 13.0962 | 8.958 | 0.59382 | 234.3276 | 1029.4613 | 2907.9311 | 465.3241 | 7179.9807 | 2610.8628 | 493.7724 | 3039.9863 | 452.313 | 799.8957
2019-09-11 |  | 80.6677 | 975.7541 | 20.2268 | 0 | 1483.0711 | 30.6099 | 151.4009 | 323.9822 | 17.7547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254.6504 | 200.5849 | 37.804 | 29.7777 | 157.097 | 123.7434 | 0 | 85.6396 | 0 | 10.1867 | 7.6091 | 17.0997 | 9.4464 | 7.4408 | 0.55938 | 241.8523 | 1042.7152 | 2900.5242 | 465.3241 | 7179.9807 | 2551.3057 | 492.0312 | 2607.2122 | 454.0883 | 696.9184
2019-09-12 |  | 73.231 | 890.6781 | 18.9018 | 0 | 1357.0079 | 27.9324 | 141.4521 | 286.6093 | 15.4494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224.3827 | 182.8832 | 34.1795 | 27.8581 | 129.4866 | 105.5381 | 0 | 76.8754 | 0 | 9.0136 | 6.9472 | 15.4519 | 8.4048 | 6.8503 | 0.55095 | 237.9972 | 1041.5157 | 3038.7745 | 465.3241 | 7179.9807 | 2543.8801 | 470.1125 | 2516.4738 | 448.2816 | 668.7625
2019-09-13 |  | 72.7203 | 889.1363 | 18.89 | 0 | 1346.23 | 27.64 | 149.254 | 265.5732 | 14.2581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207.359 | 181.4461 | 31.8087 | 27.8337 | 117.1121 | 102.477 | 0 | 73.728 | 0 | 8.3518 | 6.9351 | 15.0473 | 7.9286 | 6.9378 | 0.53332 | 230.8681 | 1037.7403 | 2904.2708 | 465.3241 | 7179.9807 | 2544.7734 | 459.1977 | 2457.5794 | 396.17 | 729.4127
2019-09-14 |  | 73.096 | 890.6227 | 18.8939 | 0 | 1363.3972 | 27.8397 | 159.6179 | 265.8359 | 14.5767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.5405 | 171.0485 | 30.6301 | 25.8676 | 114.4221 | 96.6313 | 0 | 73.7227 | 0 | 8.3613 | 6.9471 | 14.5232 | 7.7735 | 6.5649 | 0.54215 | 242.7393 | 1052.825 | 3077.9626 | 465.3241 | 7179.9807 | 2599.1004 | 456.5192 | 2432.9927 | 401.4056 | 784.014
2019-09-15 |  | 72.9763 | 890.6351 | 18.9231 | 0 | 1386.3259 | 27.7228 | 159.8708 | 265.9957 | 14.5269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.4515 | 178.28 | 31.2026 | 27.2084 | 115.3269 | 100.564 | 0 | 73.7305 | 0 | 8.3623 | 6.9468 | 14.9142 | 7.8653 | 6.8585 | 0.53419 | 240.9004 | 1045.3223 | 3045.8876 | 465.3241 | 7179.9807 | 2601.8233 | 501.3479 | 2428.2026 | 403.6827 | 775.97
2019-09-16 |  | 73.0948 | 890.9267 | 18.9514 | 0 | 1454.9975 | 27.7513 | 157.733 | 265.9747 | 14.5756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.3604 | 183.2071 | 32.1618 | 28.1442 | 116.2014 | 101.6855 | 0 | 73.7301 | 0 | 8.3644 | 6.9494 | 15.0499 | 7.9206 | 6.9312 | 0.53331 | 236.2091 | 1047.7822 | 3019.8446 | 465.3241 | 7179.9807 | 2599.788 | 506.562 | 2403.8834 | 430.5709 | 844.2985
2019-09-17 |  | 73.6924 | 891.5164 | 18.9381 | 0 | 1502.1563 | 27.9511 | 189.7763 | 360.0665 | 19.6605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275.5006 | 180.9351 | 44.7365 | 29.3807 | 172.8439 | 113.5153 | 0 | 88.0468 | 0 | 11.3247 | 6.9535 | 17.867 | 10.6576 | 6.9994 | 0.60359 | 241.9089 | 1044.6534 | 2993.5833 | 465.3241 | 7179.9807 | 2584.4741 | 492.0623 | 2605.5261 | 440.8081 | 823.6971
2019-09-18 |  | 74.0803 | 892.0066 | 18.8249 | 0 | 1472.4345 | 27.9097 | 180.5369 | 373.1074 | 20.4299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278.015 | 169.4426 | 43.7883 | 26.6878 | 204.6708 | 124.7413 | 0 | 90.1002 | 0 | 11.7216 | 6.9573 | 18.1106 | 11.0929 | 6.7608 | 0.62132 | 247.2967 | 1047.9699 | 2861.0217 | 465.3241 | 7179.9807 | 2531.4587 | 491.1238 | 2696.0103 | 438.226 | 741.1609
2019-09-19 |  | 73.4734 | 889.882 | 17.9707 | 0 | 1456.1494 | 27.8954 | 122.0362 | 266.8093 | 16.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6125 | 177.2688 | 30.1145 | 26.3476 | 115.2098 | 100.7988 | 0 | 73.1503 | 0 | 8.3883 | 7.0472 | 14.5879 | 7.6727 | 6.713 | 0.53336 | 246.2999 | 1053.4718 | 2958.7459 | 465.3241 | 7179.9807 | 2535.9837 | 492.0471 | 2410.3985 | 454.9016 | 793.0508
2019-09-20 |  | 73.0266 | 884.3345 | 19.0232 | 0 | 1495.1519 | 28.0746 | 124.5936 | 265.9186 | 15.0273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205.984 | 168.4802 | 30.6379 | 25.0597 | 116.0721 | 94.9387 | 0 | 73.0677 | 0 | 8.3574 | 6.969 | 14.1441 | 7.6672 | 6.2712 | 0.55008 | 240.2976 | 1048.7475 | 2900.9548 | 465.3241 | 7179.9807 | 2543.8676 | 498.0059 | 2272.2271 | 458.7129 | 890.8866
2019-09-21 |  | 73.5677 | 867.2447 | 19.1919 | 0 | 1507.1979 | 27.8271 | 127.0487 | 266.7045 | 15.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211.2864 | 184.8837 | 32.241 | 28.2121 | 120.0875 | 105.0812 | 0 | 73.0605 | 0 | 8.3795 | 6.96 | 15.1943 | 8.0007 | 7.0009 | 0.53332 | 256.7868 | 1059.8928 | 2875.5203 | 465.3241 | 7179.9807 | 2569.798 | 485.4061 | 1901.4804 | 459.8272 | 657.4744
2019-09-22 |  | 74.2136 | 864.8281 | 19.201 | 0 | 1397.5764 | 27.9163 | 130.085 | 266.4305 | 15.0724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207.8346 | 181.8925 | 31.491 | 27.5602 | 117.864 | 103.1521 | 0 | 73.062 | 0 | 8.3685 | 6.9588 | 14.9379 | 7.8584 | 6.8775 | 0.53328 | 248.6724 | 1052.2485 | 2751.7517 | 465.3241 | 7179.9807 | 2485.4933 | 443.0923 | 1883.697 | 455.2287 | 670.2599
2019-09-23 |  | 136.1374 | 863.9204 | 19.1727 | 0 | 1242.5328 | 27.7419 | 135.2716 | 266.9551 | 15.0555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205.2357 | 180.8844 | 30.7643 | 27.1141 | 116.6378 | 102.7987 | 0 | 73.0634 | 0 | 8.3892 | 6.9651 | 14.8335 | 7.7735 | 6.8512 | 0.53153 | 239.2927 | 1049.649 | 2813.2171 | 465.3241 | 7179.9807 | 2510.6591 | 427.9364 | 1922.9712 | 440.8323 | 709.5081
2019-09-24 |  | 158.0439 | 863.1708 | 18.6926 | 0 | 1154.1391 | 27.8589 | 136.8514 | 268.7478 | 14.732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206.7122 | 180.885 | 30.693 | 26.8581 | 118.1793 | 103.4137 | 0 | 73.0592 | 0 | 8.4489 | 6.9751 | 14.9552 | 7.8311 | 6.8526 | 0.53332 | 239.1744 | 1057.2225 | 2923.4135 | 465.3241 | 7179.9807 | 2502.3749 | 455.4037 | 1916.3282 | 438.4577 | 781.9423
2019-09-25 |  | 191.2192 | 888.9603 | 18.9822 | 0 | 1214.5465 | 27.776 | 139.208 | 268.5698 | 14.6524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.6235 | 183.4177 | 31.6656 | 27.7069 | 118.2037 | 103.4267 | 0 | 73.0593 | 0 | 8.4503 | 6.9793 | 14.9621 | 7.8299 | 6.851 | 0.53334 | 249.3567 | 1064.2714 | 2851.0929 | 465.3241 | 7179.9807 | 2504.4935 | 477.1017 | 1908.9943 | 437.5025 | 761.2443
2019-09-26 |  | 318.4999 | 889.1061 | 18.0689 | 0 | 1220.7882 | 27.791 | 143.3078 | 288.6772 | 15.6882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.8462 | 184.3107 | 31.9589 | 27.9368 | 119.1487 | 104.1536 | 0 | 73.2408 | 0 | 8.5094 | 6.9579 | 15.0115 | 7.8696 | 6.8792 | 0.53358 | 248.6317 | 1062.7132 | 2948.299 | 465.3241 | 7179.9807 | 2516.5566 | 467.1687 | 1918.5115 | 446.1218 | 710.0888
2019-09-27 |  | 73.9219 | 888.3171 | 17.871 | 0 | 1275.0824 | 27.7602 | 142.0773 | 298.2176 | 15.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.6466 | 182.5872 | 31.4236 | 27.4989 | 124.3975 | 108.8606 | 0 | 72.9243 | 0 | 8.4393 | 6.9649 | 14.8595 | 7.79 | 6.817 | 0.5333 | 257.2693 | 1074.0662 | 2904.6063 | 465.3241 | 7179.9807 | 2507.178 | 457.8672 | 1937.4331 | 432.7046 | 682.8372
2019-09-28 |  | 73.9929 | 890.5287 | 18.2596 | 0 | 1328.1393 | 27.7831 | 142.117 | 298.1223 | 15.8732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.6388 | 183.5016 | 31.7645 | 27.8042 | 124.9776 | 109.3957 | 0 | 73.4281 | 0 | 8.4379 | 6.9464 | 14.9375 | 7.8267 | 6.8509 | 0.53324 | 250.9039 | 1063.0539 | 2789.8014 | 465.3241 | 7179.9807 | 2470.2427 | 429.8124 | 1926.7855 | 416.1758 | 700.9786
2019-09-29 |  | 74.1288 | 886.7989 | 17.9428 | 0 | 1548.8638 | 27.8792 | 141.9662 | 297.8383 | 15.8201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.379 | 181.0689 | 32.1632 | 27.1657 | 125.15 | 105.7043 | 0 | 73.7239 | 0 | 8.4297 | 6.9474 | 14.6797 | 7.8188 | 6.6039 | 0.54212 | 218.9262 | 939.9745 | 2841.3288 | 465.3241 | 7179.9807 | 2453.3174 | 448.6129 | 1881.5558 | 423.3127 | 778.172
2019-09-30 |  | 123.5692 | 880.271 | 17.9068 | 0 | 1589.4387 | 27.9999 | 141.9643 | 297.8541 | 15.8602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212.9258 | 186.3502 | 32.2497 | 28.2246 | 126.9261 | 111.0842 | 0 | 73.721 | 0 | 8.4298 | 6.9627 | 15.1432 | 7.9261 | 6.9368 | 0.53328 | 251.5533 | 847.2386 | 2924.788 | 473.2821 | 5763.2022 | 2459.1476 | 458.6712 | 1891.8929 | 430.7849 | 741.9021
Monthly Chemical/Power Usage | 0 | 3030.933 | 29788.6096 | 624.6029 | 0 | 47287.232 | 936.6112 | 4770.4707 | 10741.8718 | 588.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8059.0008 | 5875.4992 | 1261.9623 | 914.511 | 5156.0217 | 3696.7816 | 0 | 2715.9147 | 0 | Total MG | Total MG | Total MG | Total MG | Total MG | Overall Ratio | 7242.0445 | 31138.4166 | 88305.5823 | 13967.6796 | 213982.6428 | 77130.0844 | 14641.0564 | 76267.0535 | 13373.6718 | 23219.1919
Cost per Gallon or lb or kW*Hr | 0.82128 | 1.4864 | 3.0825 | 4.3368 | 0 | 0.059975 | 3.739 | 0.82128 | 1.4864 | 4.3368 | 0 | 0 | 0 | 15.77 | 15.77 | 15.77 | 15.77 | 1.4864 | 1.4864 | 0.2996 | 0.2996 | 0.74349 | 0.74349 | 3.0825 | 3.0825 | 0 | 0.2996 | 0.82128 | 333.4233 | 233.6326 | 551.584 | 315.6913 | 228.6421 | 0.57996 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065
Cost Per Month | 0 | 4505.0418 | 91822.3168 | 2708.7779 | 0 | 2836.0517 | 3502.0179 | 3917.9113 | 15966.2327 | 2550.2371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2414.4766 | 1760.2996 | 938.2618 | 679.9337 | 15893.2512 | 11395.1961 | 0 | 813.688 | 0 | [6 empty] | 470.7329 | 2023.9971 | 5739.8628 | 907.8992 | 13908.8718 | 5013.4555 | 951.6687 | 4957.3585 | 869.2887 | 1509.2475
2019-09-02 | [33 empty] | Natural Gas | 248.23 | NA | 163.47 | 37.78 | 298.82 | 1074.53 | 82.45 | NA | 37.78 | 63.1
Total Binney WPF Costs |  |  | South Platte Costs |  |  | Aurora Reservoir Costs |  |  | Labor Costs | [7 empty] | Monthly Truck Loads
Chemical | 161703.6941 |  | Chemical | 119209.6354 |  | Chemical | 41680.3707 |  | Monthly | 147624.8 | [6 empty] | Chemical |  | Gallon/Lbs | Loads
Electrical | 36352.3825 | 65.9054 | Electrical | 24777.6809 |  | Electrical | 11574.7016 | [9 empty] | Ammonia |  | 2176.4733 | 0.6017
Natural Gas | 2006.16 |  | Natural Gas | 1021.2402 |  | Natural Gas | 984.9198 |  | Material Costs | [7 empty] | Anionic Polymer |  | 0 | 0
Labor | 147624.8 |  | Labor | 73812.4 |  | Labor | 73812.4 |  | Monthly | 40531.36 | [6 empty] | Carbon Dioxide |  | 47287.232 | 1.1822
Materials | 40531.36 |  | Materials | 20265.68 |  | Materials | 20265.68 | [9 empty] | Carbon PAC |  | 0 | 0
Binney MG Produced | 551.584 | 293.1624 | Net South Platte MG Produced | 228.6421 |  | Net Aurora Reservoir MG Produced | 315.6913 | [9 empty] | Cationic Polymer |  | 1212.6487 | 0.23373
Total Treated (MG) | 567.0558 |  | RWSP to Process (MG) | 233.6326 |  | RWAR to Process (MG) | 333.4233
Binney Cost per MG | 684.6211 |  | South Platte Cost per MG | 1023.3446 | 521.381 | Aurora Reservoir Cost per MG | 444.8342 | 132.0289 | [8 empty] | Chlorine |  | 16650.4147 | 1.0407
Binney Cost per KG | 0.68462 |  | South Platte Cost per KG | 1.0233 |  | Aurora Reservoir Cost per KG | 0.44483 | [9 empty] | Ferric Chloride |  | 13772.8047 | 3.5736
[17 empty] | Hydrogen Peroxide |  | 936.6112 | 0.19702
Notes: | [16 empty] | Potassium Permanganate |  | 4770.4707 | 0.37218
1. The difference between the "Binney MG Produced" and the Net numbers is the ammont of water needed from distribution to create the finished water (W3 to Chlorine and NaOH Motive) | [16 empty] | Sodium Hydroxide |  | 38641.4129 | 11.0288
Note on AF9: jamoore: Totals manually adjusted due to plant upset and waste to lagoon from finished water. Actual finished water flow less than net filter flows. Total finished water flow = 20.7549 MG. True net filter flow (gross to CCB): AR = 18.0MG, SP = 6.0MG.
Note on AG9: jamoore: Totals manually adjusted due to plant upset and waste to lagoon from finished water. Actual finished water flow less than net filter flows. Total finished water flow = 20.7549 MG. True net filter flow (gross to CCB): AR = 18.0MG, SP = 6.0MG.
Note on AH9: jamoore: Totals manually adjusted due to plant upset and waste to lagoon from finished water. Actual finished water flow less than net filter flows. Total finished water flow = 20.7549 MG. True net filter flow (gross to CCB): AR = 18.0MG, SP = 6.0MG.
Note on B40: Peter Bong: 3% Solution Strength
Note on C40: Peter Bong: 40% Solution Strength
Note on D40: Peter Bong: 50% Solution Strength
Note on E40: Peter Bong: 100% Solution Strength, PEC Cost
Note on F40: Peter Bong: 0.5% Solution Strength
Note on G40: Peter Bong: 99% Solution Strength
Note on H40: Peter Bong: 35% Solution Strength
Note on I40: Peter Bong: 3% Solution Strength
Note on J40: Peter Bong: 40% Solution Strength
Note on K40: Peter Bong: 100% Solution Strength
Note on L40: Peter Bong: 5.5% Solution Strength
Note on M40: Peter Bong: 0.5% Solution Strength
Note on N40: Peter Bong: 0.5% Solution Strength
Note on O40: Peter Bong: 100% Solution Strength
Note on P40: Peter Bong: 100% Solution Strength
Note on Q40: Peter Bong: 100% Solution Strength
Note on R40: Peter Bong: 100% Solution Strength
Note on S40: Peter Bong: 40% Solution Strength
Note on T40: Peter Bong: 40% Solution Strength
Note on U40: Peter Bong: 100% Solution Strength
Note on V40: Peter Bong: 100% Solution Strength
Note on Y40: Peter Bong: 50% Solution Strength
Note on Z40: Peter Bong: 50% Solution Strength
Note on AB40: Peter Bong: 100% Solution Strength
Note on AC40: Peter Bong: 3% Solution Strength
Note on AJ40: Peter Bong: Cost per kW*Hr
Note on AK40: Peter Bong: Cost per kW*Hr
Note on AL40: Peter Bong: Cost per kW*Hr
Note on AM40: Peter Bong: Cost per kW*Hr
Note on AN40: Peter Bong: Cost per kW*Hr
Note on AO40: Peter Bong: Cost per kW*Hr
Note on AP40: Peter Bong: Cost per kW*Hr
Note on AQ40: Peter Bong: Cost per kW*Hr
Note on AR40: Peter Bong: Cost per kW*Hr
Note on AS40: Peter Bong: Cost per kW*Hr
Note on AI42: Peter Bong: See Utility Summary Seet For Data

## OCTOBER
Current Application Point |  | Notes: Chemical are arranged in general process flow
Not in Use
[45 empty] | pass | bwpfcost
| South Platte | [6 empty] | Aurora Reservoir | [5 empty] | Filters/Adsorbers | [5 empty] | Finished Water | [6 empty] | From Chlorinator 5 | Valve Vault 1 (To Wemlinger RWAR) | RWAR Flow to Process | RWSP Flow to Process | Finished Water Flow | AR Net to Distribution | SP Net to Distribution | AR to Total Flow Blend | Blended&RW | Softening | Pre-Chem | Floc/Sed | UV/AOP | Filtration/Ad | Post-Chem | Finished | Recycle | Control
| KMnO4 (RW) | FeCl3 (Rapid Mix & Flow Split) | NaOH (Rapid Mix) | PEC/PEA (Reactors) | PEA (Sludge) | CO2 (Post Softening) | H202 (UV) | KMnO4 (RW) | FeCl3 (Rapid Mix) | PEC (Rapid Mix) | PAC (Basin 1 & 2) | PEA (Basin 1 & 2) | PEA (Sludge) | PEN AR (FIC) | PEN SP (FIC) | PEN AR (Individual Filters) | PEN SP (Individual Filters) | FeCl3 AR (Backwash Supply) | FeCl3 SP (Backwash Supply) | Cl2 AR | Cl2 SP | NH3 AR (CCB Effluent) | NH3 SP (CCB Effluent) | NaOH AR (CCB Effluent) | NaOH SP (CCB Effluent) | Fluoride(CCB Effluent) | Cl2 to RWAR, RWSP, ARFIC, or SPFIC | KMnO4 (RWAR to Wemlinger) |  |  | Total Produced From Binney
| Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Gallons per Day | MGD | MGD | MGD | MGD | MGD | Ratio | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day
2019-10-01 |  | 73.3735 | 865.1808 | 17.9674 | 0 | 1525.5903 | 28.0081 | 138.9039 | 284.5563 | 15.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.2743 | 182.2013 | 31.2138 | 27.3062 | 126.3551 | 110.5372 | 0 | 73.7216 | 0 | 8.4326 | 6.973 | 15.0636 | 7.8946 | 6.9063 | 0.53339 | 282.4351 | 864.6011 | 2744.0858 | 476.0248 | 5054.7231 | 2498.8956 | 416.9122 | 1929.5316 | 424.8248 | 563.3024
2019-10-02 |  | 73.4082 | 845.5793 | 18.0779 | 0 | 1440.4461 | 27.9612 | 139.0217 | 269.0189 | 14.7385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222.2362 | 194.3938 | 30.7018 | 26.8554 | 124.9367 | 109.2843 | 0 | 73.1278 | 0 | 8.4528 | 6.9993 | 14.9702 | 7.8734 | 6.887 | 0.53341 | 239.4723 | 821.9273 | 2792.9072 | 476.0248 | 5054.7231 | 2620.4588 | 389.6492 | 1950.6518 | 392.1546 | 603.005
2019-10-03 |  | 73.5598 | 847.5968 | 18.4895 | 0 | 1443.6469 | 27.8246 | 135.5948 | 267.0722 | 14.9175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217.2644 | 189.5807 | 30.9568 | 27.0123 | 108.82 | 94.9542 | 0 | 71.9381 | 0 | 8.3852 | 6.9972 | 14.4644 | 7.6177 | 6.647 | 0.53402 | 234.4869 | 818.7785 | 2732.6734 | 458.8315 | 5054.7231 | 2661.5687 | 387.5064 | 1880.7313 | 348.5566 | 678.5411
2019-10-04 |  | 21.285 | 243.5569 | 5.7044 | 0 | 426.0179 | 8.0709 | 159.8634 | 314.7038 | 18.5356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279.6015 | 57.3955 | 37.4233 | 7.6821 | 155.8209 | 31.9863 | 0 | 50.7686 | 0 | 9.8858 | 1.9941 | 11.3092 | 9.191 | 1.8867 | 0.82969 | 220.2878 | 785.3763 | 1429.4691 | 442.3858 | 5054.7231 | 1904.8102 | 390.7391 | 1642.6426 | 350.5142 | 721.6324
2019-10-05 |  | 0 | 0 | 0 | 0 | 0 | 0 | 167.3373 | 329.421 | 19.8468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299.4717 | 0 | 39.7828 | 0 | 184.4794 | 0 | 0 | 41.8874 | 0 | 10.3472 | 0 | 9.9463 | 9.7419 | 0 | 1 | 216.7593 | 793.3605 | 875.3664 | 442.3858 | 5054.7231 | 1654.3161 | 412.3911 | 1544.5027 | 334.1346 | 611.7125
2019-10-06 |  | 0 | 0 | 0 | 0 | 0 | 0 | 168.9067 | 334.372 | 19.8249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291.9082 | 0 | 39.4731 | 0 | 170.3082 | 0 | 0 | 41.88 | 0 | 10.3641 | 0 | 10.0008 | 9.8186 | 0 | 1 | 224.9295 | 790.7103 | 882.51 | 442.3858 | 5054.7231 | 1659.0213 | 405.2189 | 1513.0406 | 331.3554 | 522.0265
2019-10-07 |  | 0 | 0 | 0 | 0 | 0 | 0 | 169.3871 | 381.7556 | 20.7736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283.6498 | 0 | 40.1188 | 0 | 154.755 | 0 | 0 | 42.4517 | 0 | 10.4357 | 0 | 9.9931 | 9.8256 | 0 | 1 | 218.9097 | 515.0229 | 829.4865 | 442.3858 | 5054.7231 | 1658.7437 | 405.1433 | 1513.8672 | 336.615 | 689.4443
2019-10-08 |  | 0 | 0 | 0 | 0 | 0 | 0 | 137.0028 | 409.2864 | 22.4557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261.7149 | 0 | 36.4836 | 0 | 133.3554 | 0 | 0 | 41.9541 | 0 | 10.3378 | 0 | 9.3228 | 9.1825 | 0 | 1 | 210.4538 | 386.4897 | 914.9978 | 442.3858 | 5054.7231 | 1651.3181 | 423.3202 | 1546.1464 | 360.0767 | 706.2155
2019-10-09 |  | 0 | 0 | 0 | 0 | 0 | 0 | 180.3731 | 413.3259 | 23.2333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272.1567 | 0 | 39.2643 | 0 | 144.5414 | 0 | 0 | 41.8846 | 0 | 10.1618 | 0 | 9.7454 | 9.5731 | 0 | 1 | 217.3152 | 390.6246 | 878.4353 | 442.3858 | 5054.7231 | 1597.9021 | 439.3046 | 1531.3675 | 385.3234 | 674.1574
2019-10-10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 64.6646 | 186.2149 | 8.1475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163.6394 | 0 | 14.5813 | 0 | 52.0333 | 0 | 0 | 20.8558 | 0 | 3.5616 | 0 | 3.46 | 3.394 | 0 | 1 | 264.4103 | 518.4945 | 817.5265 | 442.3858 | 5054.7231 | 1583.5385 | 509.4484 | 852.2307 | 187.082 | 605.4807
2019-10-11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.0302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272.0407 | 572.9944 | 887.2577 | 442.3858 | 5054.7231 | 1597.7287 | 553.037 | 405.4559 | 81.8584 | 595.75
2019-10-12 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.2382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.0585 | 516.5429 | 966.2102 | 442.3858 | 5054.7231 | 1557.9044 | 436.2192 | 369.8412 | 81.0321 | 631.9503
2019-10-13 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.2434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.0636 | 504.9769 | 914.8149 | 442.3858 | 5054.7231 | 1555.6247 | 408.1685 | 320.1244 | 74.481 | 691.9558
2019-10-14 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.2456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222.0767 | 571.2499 | 1061.363 | 442.3858 | 5054.7231 | 1568.2901 | 400.9031 | 291.0256 | 78.7921 | 727.1114
2019-10-15 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.0147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.2086 | 481.9017 | 787.6299 | 442.3858 | 5054.7231 | 1561.0619 | 399.6888 | 308.8024 | 74.0227 | 566.9514
2019-10-16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69521 | 0 | 0 | 0 | 262.7097 | 0 | 0.006969 | 0 | 0 | 0 | 0 | 0 | 215.8655 | 522.3758 | 779.1812 | 442.3858 | 5054.7231 | 1572.92 | 404.8401 | 297.8367 | 73.905 | 711.9032
2019-10-17 |  | 0 | 0 | 0 | 0 | 0 | 0 | 101.6148 | 236.524 | 12.6696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.4376 | 0 | 5.6754 | 0 | 0 | 0 | 0 | 0 | 214.142 | 555.3549 | 779.1812 | 442.3858 | 5054.7231 | 1559.7295 | 426.3544 | 262.9958 | 200.6 | 722.7621
2019-10-18 |  | 0 | 0 | 0 | 0 | 0 | 0 | 209.395 | 487.6309 | 27.0931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198.6456 | 0 | 26.5608 | 0 | 101.0911 | 0 | 0 | 49.116 | 0 | 11.9909 | 0 | 4.8312 | 6.9796 | 0 | 1 | 220.1203 | 501.9162 | 779.1812 | 442.3858 | 5054.7231 | 1574.0655 | 433.4823 | 1148.1632 | 286.1921 | 645.9342
2019-10-19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 183.8674 | 420.3387 | 23.0023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262.3075 | 0 | 39.8645 | 0 | 142.8021 | 0 | 0 | 41.9023 | 0 | 10.3363 | 0 | 9.6238 | 9.4537 | 0 | 1 | 218.7075 | 494.7357 | 779.1812 | 442.3858 | 5054.7231 | 1602.7211 | 417.1355 | 1698.0985 | 268.8408 | 569.9193
2019-10-20 |  | 0 | 0 | 0 | 0 | 0 | 0 | 184.1713 | 420.2879 | 23.1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.6677 | 0 | 41.4164 | 0 | 140.9056 | 0 | 0 | 41.8747 | 0 | 10.3325 | 0 | 9.8698 | 9.7153 | 0 | 1 | 242.5507 | 496.2666 | 779.1812 | 442.3858 | 5054.7231 | 1600.6615 | 425.7173 | 1775.1176 | 272.8803 | 566.3143
2019-10-21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 186.4331 | 425.5498 | 23.2774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261.346 | 0 | 40.825 | 0 | 139.904 | 0 | 0 | 42.6957 | 0 | 10.4616 | 0 | 9.834 | 9.6848 | 0 | 1 | 249.6976 | 521.2646 | 779.1812 | 442.3858 | 5054.7231 | 1620.65 | 469.0132 | 1689.6452 | 299.36 | 571.5043
2019-10-22 |  | 0 | 0 | 0 | 0 | 0 | 0 | 194.7333 | 444.7018 | 24.4477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.7145 | 0 | 40.0692 | 0 | 142.3836 | 0 | 0 | 45.1438 | 0 | 10.9333 | 0 | 9.6903 | 9.5271 | 0 | 1 | 238.6253 | 514.0601 | 779.1812 | 442.3858 | 5054.7231 | 1589.0747 | 462.6414 | 1822.4112 | 303.2865 | 629.9659
2019-10-23 |  | 0 | 0 | 0 | 0 | 0 | 0 | 175.5151 | 396.634 | 21.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.556 | 0 | 40.2639 | 0 | 105.4216 | 0 | 0 | 41.8768 | 0 | 10.3246 | 0 | 10.0033 | 9.8559 | 0 | 1 | 240.8216 | 510.1214 | 779.1812 | 442.3858 | 5054.7231 | 1571.9512 | 473.1994 | 1835.151 | 281.4888 | 582.6258
2019-10-24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 167.4193 | 406.2439 | 22.9826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262.7196 | 0 | 40.7045 | 0 | 107.3428 | 0 | 0 | 42.3383 | 0 | 10.3539 | 0 | 9.8753 | 9.7263 | 0 | 1 | 250.087 | 528.2775 | 779.1812 | 442.3858 | 5054.7231 | 1612.9435 | 502.5847 | 1868.1531 | 284.4228 | 576.5775
2019-10-25 |  | 0 | 0 | 0 | 0 | 0 | 0 | 173.548 | 424.2011 | 25.0202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258.9818 | 0 | 38.9095 | 0 | 109.6642 | 0 | 0 | 42.5289 | 0 | 10.4266 | 0 | 9.8095 | 9.6686 | 0 | 1 | 209.9476 | 461.8048 | 779.1812 | 442.3858 | 5054.7231 | 1559.0767 | 439.5884 | 1839.2801 | 296.4468 | 582.9577
2019-10-26 |  | 0 | 0 | 0 | 0 | 0 | 0 | 190.0402 | 426.7401 | 25.0613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.7871 | 0 | 39.1827 | 0 | 127.8363 | 0 | 0 | 43.0259 | 0 | 10.4902 | 0 | 9.7742 | 9.6085 | 0 | 1 | 168.4922 | 417.6761 | 826.8123 | 442.3858 | 5054.7231 | 1534.1889 | 409.8335 | 1785.8948 | 319.2087 | 659.8327
2019-10-27 |  | 0 | 0 | 0 | 0 | 0 | 0 | 189.3086 | 424.4323 | 24.9739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270.4986 | 0 | 41.2406 | 0 | 155.9627 | 0 | 0 | 41.8675 | 0 | 10.4338 | 0 | 10.2409 | 10.0004 | 0 | 1 | 206.1083 | 415.6817 | 820.4139 | 442.3858 | 5054.7231 | 1649.0686 | 527.0224 | 1847.4568 | 290.0569 | 593.6854
2019-10-28 |  | 0 | 0 | 0 | 0 | 0 | 0 | 189.1668 | 425.0729 | 24.9964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267.3883 | 0 | 40.861 | 0 | 144.2726 | 0 | 0 | 42.716 | 0 | 10.4551 | 0 | 10.1174 | 9.8613 | 0 | 1 | 227.9018 | 495.2799 | 827.9252 | 538.769 | 3324.0358 | 1699.1333 | 608.0153 | 1885.692 | 294.1852 | 666.167
2019-10-29 |  | 0 | 0 | 0 | 0 | 0 | 0 | 189.58 | 424.9409 | 25.1474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.5935 | 0 | 39.6779 | 0 | 139.8759 | 0 | 0 | 43.8283 | 0 | 10.4526 | 0 | 9.7617 | 9.5188 | 0 | 1 | 248.5445 | 551.2638 | 826.3171 | 677.2869 | 1152.6274 | 1829.9927 | 623.9044 | 1897.9883 | 353.7336 | 583.555
2019-10-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 193.5507 | 433.9929 | 25.6903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256.035 | 0 | 37.7671 | 0 | 127.4481 | 0 | 0 | 43.5924 | 0 | 10.6704 | 0 | 9.6141 | 9.4002 | 0 | 1 | 288.4001 | 644.2012 | 906.2617 | 677.2869 | 1152.6274 | 1886.1213 | 634.1493 | 1890.6 | 391.3779 | 577.412
2019-10-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 187.5248 | 420.3842 | 25.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265.6683 | 0 | 39.7901 | 0 | 116.6794 | 0 | 0 | 42.48 | 0 | 10.3383 | 0 | 9.8351 | 9.7352 | 0 | 1 | 266.9443 | 601.4953 | 941.3747 | 677.2869 | 1152.6274 | 1755.7313 | 558.0197 | 1900.7972 | 341.8431 | 582.4798
Monthly Chemical/Power Usage | 0 | 241.6265 | 2801.9138 | 60.2391 | 0 | 4835.7011 | 91.8648 | 4176.9239 | 9411.5112 | 532.6725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6105.8266 | 623.5712 | 887.1326 | 89.5513 | 3156.9955 | 346.762 | 0 | 1653.3756 | 0 | Total MG | Total MG | Total MG | Total MG | Total MG | Overall Ratio | 7215.8641 | 17564.8269 | 32455.65 | 14598.7708 | 143259.4429 | 53549.2128 | 14193.1513 | 43045.2435 | 8398.6518 | 19412.8329
Cost per Gallon or lb or kW*Hr | 0.82128 | 1.4864 | 2.954 | 4.3368 | 0 | 0.059975 | 3.739 | 0.82128 | 1.4864 | 4.3368 | 0 | 0 | 0 | 15.77 | 15.77 | 15.77 | 15.77 | 1.4864 | 1.4864 | 0.2996 | 0.2996 | 0.74349 | 0.74349 | 2.954 | 2.954 | 0 | 0.2996 | 0.82128 | 244.0473 | 22.9636 | 241.1565 | 216.848 | 22.3271 | 0.90665 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07
Cost Per Month | 0 | 359.1427 | 8276.9319 | 261.245 | 0 | 290.0212 | 343.4854 | 3430.4408 | 13988.8448 | 2310.0941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1829.3057 | 186.8219 | 659.5781 | 66.5809 | 9325.8531 | 1024.3445 | 0 | 495.3513 | 0 | [6 empty] | 505.1105 | 1229.5379 | 2271.8955 | 1021.914 | 10028.161 | 3748.4449 | 993.5206 | 3013.167 | 587.9056 | 1358.8983
2019-10-02 | [33 empty] | Natural Gas | 404.28 | NA | 934.84 | 37.78 | 624.27 | 1286.51 | 192.6 | NA | 41.5 | 94.91
Total Binney WPF Costs |  |  | South Platte Costs |  |  | Aurora Reservoir Costs |  |  | Labor Costs | [7 empty] | Monthly Truck Loads
Chemical | 42848.0413 |  | Chemical | 10808.5735 |  | Chemical | 31544.1165 |  | Monthly | 152411.47 | [6 empty] | Chemical |  | Gallon/Lbs | Loads
Electrical | 24758.5553 |  | Electrical | 14138.1452 |  | Electrical | 10620.4101 | [9 empty] | Ammonia |  | 976.6839 | 0.27001
Natural Gas | 3616.69 |  | Natural Gas | 1335.7101 |  | Natural Gas | 2280.9799 |  | Material Costs | [7 empty] | Anionic Polymer |  | 0 | 0
Labor | 152411.47 |  | Labor | 76205.735 |  | Labor | 76205.735 |  | Monthly | 30698.77 | [6 empty] | Carbon Dioxide |  | 4835.7011 | 0.12089
Materials | 30698.77 |  | Materials | 15349.385 |  | Materials | 15349.385 | [9 empty] | Carbon PAC |  | 0 | 0
Binney MG Produced | 241.1565 |  | Net South Platte MG Produced | 22.3271 |  | Net Aurora Reservoir MG Produced | 216.848 | [9 empty] | Cationic Polymer |  | 592.9116 | 0.11428
Total Treated (MG) | 267.0109 |  | RWSP to Process (MG) | 22.9636 |  | RWAR to Process (MG) | 244.0473
Binney Cost per MG | 952.5213 |  | South Platte Cost per MG | 5131.4925 |  | Aurora Reservoir Cost per MG | 557.2717 | [9 empty] | Chlorine |  | 8382.7735 | 0.52392
Binney Cost per KG | 0.95252 |  | South Platte Cost per KG | 5.1315 | 484.1015 | Aurora Reservoir Cost per KG | 0.55727 | 145.4665 | [8 empty] | Ferric Chloride |  | 9653.1377 | 2.5047
[17 empty] | Hydrogen Peroxide |  | 91.8648 | 0.019324
Notes: | [16 empty] | Potassium Permanganate |  | 4176.9239 | 0.32587
1. The difference between the "Binney MG Produced" and the Net numbers is the ammont of water needed from distribution to create the finished water (W3 to Chlorine and NaOH Motive) | [16 empty] | Sodium Hydroxide |  | 6305.6712 | 1.7997
Note on AF9: jamoore: Totals manually adjusted due to plant upset and waste to lagoon from finished water. Actual finished water flow less than net filter flows. Total finished water flow = 20.7549 MG. True net filter flow (gross to CCB): AR = 18.0MG, SP = 6.0MG.
Note on AG9: jamoore: Totals manually adjusted due to plant upset and waste to lagoon from finished water. Actual finished water flow less than net filter flows. Total finished water flow = 20.7549 MG. True net filter flow (gross to CCB): AR = 18.0MG, SP = 6.0MG.
Note on AH9: jamoore: Totals manually adjusted due to plant upset and waste to lagoon from finished water. Actual finished water flow less than net filter flows. Total finished water flow = 20.7549 MG. True net filter flow (gross to CCB): AR = 18.0MG, SP = 6.0MG.
Note on B40: Peter Bong: 3% Solution Strength
Note on C40: Peter Bong: 40% Solution Strength
Note on D40: Peter Bong: 50% Solution Strength
Note on E40: Peter Bong: 100% Solution Strength, PEC Cost
Note on F40: Peter Bong: 0.5% Solution Strength
Note on G40: Peter Bong: 99% Solution Strength
Note on H40: Peter Bong: 35% Solution Strength
Note on I40: Peter Bong: 3% Solution Strength
Note on J40: Peter Bong: 40% Solution Strength
Note on K40: Peter Bong: 100% Solution Strength
Note on L40: Peter Bong: 5.5% Solution Strength
Note on M40: Peter Bong: 0.5% Solution Strength
Note on N40: Peter Bong: 0.5% Solution Strength
Note on O40: Peter Bong: 100% Solution Strength
Note on P40: Peter Bong: 100% Solution Strength
Note on Q40: Peter Bong: 100% Solution Strength
Note on R40: Peter Bong: 100% Solution Strength
Note on S40: Peter Bong: 40% Solution Strength
Note on T40: Peter Bong: 40% Solution Strength
Note on U40: Peter Bong: 100% Solution Strength
Note on V40: Peter Bong: 100% Solution Strength
Note on Y40: Peter Bong: 50% Solution Strength
Note on Z40: Peter Bong: 50% Solution Strength
Note on AB40: Peter Bong: 100% Solution Strength
Note on AC40: Peter Bong: 3% Solution Strength
Note on AJ40: Peter Bong: Cost per kW*Hr
Note on AK40: Peter Bong: Cost per kW*Hr
Note on AL40: Peter Bong: Cost per kW*Hr
Note on AM40: Peter Bong: Cost per kW*Hr
Note on AN40: Peter Bong: Cost per kW*Hr
Note on AO40: Peter Bong: Cost per kW*Hr
Note on AP40: Peter Bong: Cost per kW*Hr
Note on AQ40: Peter Bong: Cost per kW*Hr
Note on AR40: Peter Bong: Cost per kW*Hr
Note on AS40: Peter Bong: Cost per kW*Hr
Note on AI42: Peter Bong: See Utility Summary Seet For Data

## NOVEMBER
Current Application Point |  | Notes: Chemical are arranged in general process flow
Not in Use
[45 empty] | pass | bwpfcost
| South Platte | [6 empty] | Aurora Reservoir | [5 empty] | Filters/Adsorbers | [5 empty] | Finished Water | [6 empty] | From Chlorinator 5 | Valve Vault 1 (To Wemlinger RWAR) | RWAR Flow to Process | RWSP Flow to Process | Finished Water Flow | AR Net to Distribution | SP Net to Distribution | AR to Total Flow Blend | Blended&RW | Softening | Pre-Chem | Floc/Sed | UV/AOP | Filtration/Ad | Post-Chem | Finished | Recycle | Control
| KMnO4 (RW) | FeCl3 (Rapid Mix & Flow Split) | NaOH (Rapid Mix) | PEC/PEA (Reactors) | PEA (Sludge) | CO2 (Post Softening) | H202 (UV) | KMnO4 (RW) | FeCl3 (Rapid Mix) | PEC (Rapid Mix) | PAC (Basin 1 & 2) | PEA (Basin 1 & 2) | PEA (Sludge) | PEN AR (FIC) | PEN SP (FIC) | PEN AR (Individual Filters) | PEN SP (Individual Filters) | FeCl3 AR (Backwash Supply) | FeCl3 SP (Backwash Supply) | Cl2 AR | Cl2 SP | NH3 AR (CCB Effluent) | NH3 SP (CCB Effluent) | NaOH AR (CCB Effluent) | NaOH SP (CCB Effluent) | Fluoride(CCB Effluent) | Cl2 to RWAR, RWSP, ARFIC, or SPFIC | KMnO4 (RWAR to Wemlinger) |  |  | Total Produced From Binney
| Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Gallons per Day | MGD | MGD | MGD | MGD | MGD | Ratio | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day
2019-11-01 |  | 0 | 0 | 0 | 0 | 0 | 0 | 188.4836 | 419.0786 | 25.5079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260.4852 | 0 | 38.9379 | 0 | 115.4015 | 0 | 0 | 42.5319 | 0 | 10.3044 | 0 | 9.7114 | 9.6061 | 0 | 1 | 251.2629 | 550.3898 | 872.3098 | 677.2869 | 1152.6274 | 1744.2898 | 524.8889 | 1902.6962 | 350.1342 | 589.8371
2019-11-02 |  | 0 | 0 | 0 | 0 | 0 | 0 | 190.7759 | 419.9042 | 25.5246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269.4282 | 0 | 39.0644 | 0 | 122.0538 | 0 | 0 | 42.5324 | 0 | 10.3233 | 0 | 9.8983 | 9.806 | 0 | 1 | 240.79 | 541.3819 | 938.4822 | 677.2869 | 1152.6274 | 1664.7753 | 505.7132 | 1904.015 | 357.2537 | 534.3079
2019-11-03 |  | 0 | 0 | 0 | 0 | 0 | 0 | 192.5284 | 424.0202 | 25.5538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276.9918 | 0 | 39.7817 | 0 | 135.0425 | 0 | 0 | 42.5478 | 0 | 10.4221 | 0 | 9.8223 | 9.5097 | 0 | 1 | 228.6696 | 507.5588 | 874.2888 | 677.2869 | 1152.6274 | 1740.4671 | 467.7837 | 1904.8736 | 352.0364 | 509.6845
2019-11-04 |  | 0 | 0 | 0 | 0 | 0 | 0 | 191.4398 | 421.4347 | 25.1968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299.8194 | 0 | 39.8757 | 0 | 166.8937 | 0 | 0 | 42.2734 | 0 | 10.3579 | 0 | 9.8236 | 9.8052 | 0 | 1 | 225.9009 | 505.437 | 891.9958 | 677.2869 | 1152.6274 | 1714.1398 | 458.2974 | 1858.2631 | 349.099 | 575.1319
2019-11-05 |  | 0 | 0 | 0 | 0 | 0 | 0 | 191.1793 | 420.8729 | 25.4328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289.562 | 0 | 39.2041 | 0 | 157.5749 | 0 | 0 | 44.742 | 0 | 10.3457 | 0 | 9.8457 | 9.7331 | 0 | 1 | 241.9927 | 518.082 | 868.1252 | 677.2869 | 1152.6274 | 1630.897 | 453.1175 | 1876.6985 | 348.099 | 593.1802
2019-11-06 |  | 0 | 0 | 0 | 0 | 0 | 0 | 190.6499 | 419.8097 | 25.4611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292.8426 | 0 | 40.5145 | 0 | 157.8299 | 0 | 0 | 46.4574 | 0 | 10.3253 | 0 | 10.0089 | 9.8785 | 0 | 1 | 231.3131 | 519.1078 | 872.1834 | 677.2869 | 1152.6274 | 1649.6311 | 467.9708 | 1837.7903 | 350.2248 | 571.6415
2019-11-07 |  | 0 | 0 | 0 | 0 | 0 | 0 | 195.1227 | 426.2256 | 25.4314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267.8127 | 0 | 38.5079 | 0 | 151.8866 | 0 | 0 | 46.7053 | 0 | 10.4797 | 0 | 9.6216 | 9.4864 | 0 | 1 | 239.7756 | 530.4584 | 872.4914 | 677.2869 | 1152.6274 | 1797.9487 | 489.3653 | 1946.3481 | 353.7017 | 541.5096
2019-11-08 |  | 0 | 0 | 0 | 0 | 0 | 0 | 191.2322 | 421.2276 | 24.9503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.8234 | 0 | 38.7948 | 0 | 153.7054 | 0 | 0 | 45.8039 | 0 | 10.3561 | 0 | 9.6955 | 9.5655 | 0 | 1 | 227.067 | 507.2526 | 938.2651 | 677.2869 | 1152.6274 | 1656.9049 | 445.0089 | 1896.8335 | 349.28 | 647.1015
2019-11-09 |  | 0 | 0 | 0 | 0 | 0 | 0 | 190.9222 | 420.1763 | 24.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.3184 | 0 | 39.1806 | 0 | 154.1857 | 0 | 0 | 46.0029 | 0 | 10.3286 | 0 | 9.8881 | 9.7534 | 0 | 1 | 230.3426 | 552.8222 | 935.8432 | 511.8463 | 1152.6274 | 1630.8883 | 418.871 | 1863.8089 | 349.1742 | 699.3857
2019-11-10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 191.0154 | 420.4927 | 24.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261.2119 | 0 | 39.284 | 0 | 156.1476 | 0 | 0 | 46.4646 | 0 | 10.3365 | 0 | 10.0069 | 9.8809 | 0 | 1 | 220.3608 | 527.6452 | 871.6132 | 447.1087 | 1152.6274 | 1607.5229 | 414.8842 | 1856.2283 | 348.1075 | 630.7736
2019-11-11 |  | 0 | 0 | 0.54625 | 0 | 0 | 0 | 190.8287 | 420.4699 | 24.9364 | 0.001133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256.2209 | 0 | 38.2778 | 0 | 152.6359 | 0 | 0 | 47.2009 | 0 | 10.3365 | 2.3291 | 9.8219 | 9.6854 | 0 | 1 | 252.4276 | 556.0182 | 883.8377 | 447.1087 | 1334.6735 | 1696.9298 | 830.2243 | 1926.0811 | 362.4245 | 544.0399
2019-11-12 |  | 0 | 0 | 0.54583 | 0 | 0 | 0 | 195.5639 | 423.568 | 25.3862 | 0.0011235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.2023 | 0 | 37.8658 | 0 | 150.8373 | 0 | 0 | 47.2352 | 0 | 10.4131 | 2.5345 | 9.8298 | 9.7002 | 0 | 1 | 239.4378 | 536.2557 | 935.1318 | 447.1087 | 1773.1272 | 1745.4911 | 771.2791 | 1912.8121 | 356.4585 | 580.187
2019-11-13 |  | 0 | 0 | 0.55304 | 0 | 0 | 0 | 196.3397 | 424.7615 | 25.3742 | 0.0041448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.7078 | 0 | 39.3262 | 0 | 153.0743 | 0 | 0 | 47.1427 | 0 | 10.4407 | 1.172 | 10.0375 | 9.889 | 0 | 1 | 220.7099 | 508.6907 | 869.645 | 447.1087 | 1842.5755 | 1613.6861 | 439.0633 | 1939.6852 | 343.3462 | 572.0665
2019-11-14 |  | 0 | 0 | 0.56019 | 0 | 0 | 0 | 194.1846 | 420.215 | 25.2183 | 0.0026908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262.5397 | 0 | 39.3916 | 0 | 153.3897 | 0 | 0 | 45.7992 | 0 | 10.3299 | 0 | 9.9558 | 9.8248 | 0 | 1 | 226.6846 | 512.7241 | 892.0037 | 447.1087 | 1842.5755 | 1658.1084 | 461.2263 | 2002.4948 | 319.7064 | 587.416
2019-11-15 |  | 0 | 0 | 0.56003 | 0 | 0 | 0 | 245.8552 | 532.2028 | 31.7584 | 0.0040125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308.8334 | 0 | 48.6982 | 0 | 181.5401 | 0 | 0 | 58.7443 | 0 | 13.0891 | 0 | 11.9638 | 11.8308 | 0 | 1 | 222.8739 | 512.4038 | 897.4702 | 447.1087 | 1842.5755 | 1664.1785 | 442.5691 | 2350.5115 | 327.0927 | 691.4143
2019-11-16 |  | 0 | 0 | 0.56127 | 0 | 0 | 0 | 269.1722 | 582.3134 | 34.8561 | 0.006609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350.313 | 0 | 56.9408 | 0 | 203.1173 | 0 | 0 | 64.5033 | 0 | 14.3192 | 0 | 13.9323 | 13.7706 | 0 | 1 | 218.6722 | 517.6928 | 965.7244 | 447.1087 | 1842.5755 | 1603.9349 | 436.1654 | 2605.8383 | 319.4901 | 599.1551
2019-11-17 |  | 0 | 0 | 0.56175 | 0 | 0 | 0 | 263.3301 | 582.9494 | 35.204 | 0.0059292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.9709 | 0 | 56.8005 | 0 | 208.7114 | 0 | 0 | 64.4255 | 0 | 14.3338 | 0 | 14.0103 | 13.8706 | 0 | 1 | 229.7765 | 524.9041 | 891.0869 | 447.1087 | 1842.5755 | 1609.6026 | 446.5913 | 2628.1093 | 292.2699 | 549.2472
2019-11-18 |  | 0 | 0 | 0.56191 | 0 | 0 | 0 | 255.5804 | 583.1421 | 35.1822 | 0.0073265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346.1946 | 0 | 54.7718 | 0 | 211.1414 | 0 | 0 | 64.4261 | 0 | 14.34 | 0 | 13.96 | 13.8031 | 0 | 1 | 228.1031 | 538.9818 | 916.9105 | 447.1087 | 1842.5755 | 1651.9356 | 387.295 | 2590.3994 | 287.0155 | 627.7692
2019-11-19 |  | 0 | 0 | 0.56448 | 0 | 0 | 0 | 261.7025 | 584.7753 | 35.2179 | 0.007487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345.4433 | 0 | 54.4245 | 0 | 207.746 | 0 | 0 | 64.4254 | 0 | 14.3799 | 0.069212 | 13.6448 | 13.4861 | 0 | 1 | 213.3293 | 509.9818 | 901.1575 | 447.2653 | 1842.5755 | 1734.2966 | 399.9269 | 2585.329 | 291.4081 | 679.969
2019-11-20 |  | 0 | 0 | 0.56047 | 0 | 0 | 0 | 266.3696 | 585.9168 | 35.1317 | 0.0068825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.843 | 0 | 52.8315 | 0 | 222.7171 | 0 | 0 | 65.1003 | 0 | 14.4083 | 0.0010598 | 13.7186 | 13.4829 | 0 | 1 | 223.1414 | 509.7802 | 844.6065 | 447.4643 | 1842.5755 | 1696.275 | 448.9829 | 2592.2345 | 291.5697 | 592.9636
2019-11-21 |  | 0 | 0 | 0.55124 | 0 | 0 | 0 | 243.6108 | 545.7972 | 32.5345 | 0.0015201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342.6052 | 0 | 50.2749 | 0 | 209.2641 | 0 | 0 | 61.5139 | 0 | 13.4212 | 0 | 13.1094 | 12.8992 | 0 | 1 | 255.6182 | 555.5889 | 901.5098 | 484.2068 | 1842.5755 | 1701.5984 | 526.9587 | 2498.8763 | 305.9494 | 623.4909
2019-11-22 |  | 0 | 0 | 0.54607 | 0 | 0 | 0 | 225.5232 | 504.6341 | 29.9722 | 0.0031534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314.6318 | 0 | 45.6111 | 0 | 186.5876 | 0 | 0 | 57.0885 | 0 | 12.4069 | 0 | 11.8155 | 11.6081 | 0 | 1 | 256.3297 | 563.8328 | 870.8324 | 565.8295 | 1842.5755 | 1712.4658 | 531.7421 | 2282.3914 | 338.8471 | 578.478
2019-11-23 |  | 0 | 0 | 0.54932 | 0 | 0 | 0 | 224.7968 | 503.6196 | 29.9671 | 0.0065237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.7572 | 0 | 45.7006 | 0 | 183.3186 | 0 | 0 | 56.8714 | 0 | 12.384 | 0 | 11.6375 | 11.431 | 0 | 1 | 247.5529 | 548.6774 | 980.3039 | 510.594 | 1842.5755 | 1762.7861 | 485.92 | 2293.9124 | 366.2678 | 570.2988
2019-11-24 |  | 0 | 0 | 0.55447 | 0 | 0 | 0 | 223.0637 | 500.5457 | 29.9672 | 0.0091474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304.0056 | 0 | 45.6888 | 0 | 182.8066 | 0 | 0 | 55.7872 | 0 | 12.3068 | 0 | 11.4691 | 11.3615 | 0 | 1 | 233.2924 | 511.6848 | 906.3656 | 467.1458 | 1842.5755 | 1764.1307 | 437.9798 | 2244.2683 | 365.929 | 597.7732
2019-11-25 |  | 0 | 0 | 0.55448 | 0 | 0 | 0 | 209.9271 | 467.5675 | 27.8775 | 0.010592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288.7327 | 0 | 43.1346 | 0 | 157.6573 | 0 | 0 | 51.5964 | 0 | 11.4945 | 0.0010297 | 11.0334 | 10.9138 | 0 | 1 | 237.4093 | 523.5915 | 908.4379 | 486.1977 | 1842.5755 | 1695.0184 | 472.3874 | 2172.1113 | 395.2839 | 585.7322
2019-11-26 |  | 0 | 0 | 0.52125 | 0 | 0 | 0 | 190.4518 | 418.9722 | 24.5252 | 0.0051833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272.0433 | 0 | 37.7853 | 0 | 139.8283 | 0 | 0 | 45.5031 | 0 | 10.2999 | 0 | 9.8681 | 9.7637 | 0 | 1 | 267.0179 | 602.7617 | 938.9222 | 544.4201 | 1813.9275 | 1709.6047 | 814.8929 | 1982.2117 | 450.3519 | 554.2934
2019-11-27 |  | 0 | 0 | 0.52885 | 0 | 0 | 0 | 195.9549 | 423.8334 | 24.7949 | 0.0050228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268.3018 | 0 | 36.7823 | 0 | 140.6639 | 0 | 0 | 45.9107 | 0 | 10.4188 | 0 | 9.6878 | 9.5655 | 0 | 1 | 271.8654 | 652.7232 | 978.6202 | 546.13 | 1807.8726 | 1828.432 | 1128.675 | 1983.6648 | 462.8271 | 578.2727
2019-11-28 |  | 0 | 0 | 0.52487 | 0 | 0 | 0 | 195.8854 | 423.1129 | 24.9069 | 0.0089026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274.3744 | 0 | 38.1594 | 0 | 153.9264 | 0 | 0 | 46.1526 | 0 | 10.4031 | 0 | 9.9381 | 9.8025 | 0 | 1 | 269.9697 | 624.5221 | 978.6797 | 546.13 | 1807.8726 | 1755.1475 | 1121.3935 | 1902.3018 | 459.7342 | 565.2885
2019-11-29 |  | 0 | 0 | 0.53082 | 0 | 0 | 0 | 194.7076 | 421.1275 | 25.1513 | 0.012215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268.3209 | 0 | 38.7634 | 0 | 159.7815 | 0 | 0 | 45.8034 | 0 | 10.3519 | 0 | 9.919 | 9.7729 | 0 | 1 | 259.5009 | 585.3842 | 927.3465 | 546.13 | 1807.8726 | 1799.7567 | 1086.6756 | 1923.1699 | 439.3166 | 547.7764
2019-11-30 |  | 0 | 0 | 0.53083 | 0 | 0 | 0 | 194.5565 | 420.7239 | 25.1651 | 0.015428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266.4994 | 0 | 38.5241 | 0 | 153.1271 | 0 | 0 | 45.805 | 0 | 10.3434 | 0 | 9.8785 | 9.7283 | 0 | 1 | 261.2925 | 606.3784 | 950.3209 | 546.13 | 1807.8726 | 1691.7466 | 1086.8635 | 1920.4744 | 440.3906 | 565.359
Monthly Chemical/Power Usage | 0 | 0 | 0 | 10.9674 | 0 | 0 | 0 | 6350.7541 | 13983.4905 | 835.7387 | 0.12503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8740.8367 | 0 | 1292.8986 | 0 | 4982.5934 | 0 | 0 | 1527.0967 | 0 | Total MG | Total MG | Total MG | Total MG | Total MG | Overall Ratio | 7172.4805 | 16262.7139 | 27274.5115 | 16091.7632 | 47632.9743 | 50932.5906 | 17402.7131 | 63184.4329 | 10722.7897 | 17683.5444
Cost per Gallon or lb or kW*Hr | 0.82128 | 1.4864 | 2.954 | 4.3368 | 0 | 0.059975 | 3.739 | 0.82128 | 1.4864 | 4.3368 | 0 | 0 | 0 | 15.77 | 15.77 | 15.77 | 15.77 | 1.4864 | 1.4864 | 0.2996 | 0.2996 | 0.74349 | 0.74349 | 2.954 | 2.954 | 0 | 0.2996 | 0.82128 | 343.8006 | 6.107 | 327.5537 | 323.2148 | 0 | 1 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066
Cost Per Month | 0 | 0 | 0 | 47.5635 | 0 | 0 | 0 | 5215.7727 | 20784.4283 | 3624.4317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2618.7547 | 0 | 961.2628 | 0 | 14718.7205 | 0 | 0 | 457.5182 | 0 | [6 empty] | 473.3837 | 1073.3391 | 1800.1178 | 1062.0564 | 3143.7763 | 3361.551 | 1148.5791 | 4170.1726 | 707.7041 | 1167.1139
2019-11-02 | [33 empty] | Natural Gas | 932.27 | NA | 1813.6 | 697.44 | 1094.55 | 2933.61 | 1096.86 | NA | 173.23 | 401.48
Total Binney WPF Costs |  |  | South Platte Costs |  |  | Aurora Reservoir Costs |  |  | Labor Costs | [7 empty] | Monthly Truck Loads
Chemical | 48428.4523 |  | Chemical | 47.5635 |  | Chemical | 47923.3706 |  | Monthly | 152536.09 | [6 empty] | Chemical |  | Gallon/Lbs | Loads
Electrical | 18107.7939 |  | Electrical | 6054.5833 |  | Electrical | 12053.2106 | [9 empty] | Ammonia |  | 1292.8986 | 0.35743
Natural Gas | 9143.04 |  | Natural Gas | 2288.705 |  | Natural Gas | 6854.335 |  | Material Costs | [7 empty] | Anionic Polymer |  | 0 | 0
Labor | 152536.09 |  | Labor | 76268.045 |  | Labor | 76268.045 |  | Monthly | 49925.01 | [6 empty] | Carbon Dioxide |  | 0 | 0
Materials | 49925.01 |  | Materials | 24962.505 |  | Materials | 24962.505 | [9 empty] | Carbon PAC |  | 0.12503 | 0.12495
Binney MG Produced | 327.5537 |  | Net South Platte MG Produced | 0 |  | Net Aurora Reservoir MG Produced | 323.2148 | [9 empty] | Cationic Polymer |  | 846.7062 | 0.1632
Total Treated (MG) | 349.9076 |  | RWSP to Process (MG) | 6.107 |  | RWAR to Process (MG) | 343.8006
Binney Cost per MG | 794.8966 |  | South Platte Cost per MG | 17950.199 |  | Aurora Reservoir Cost per MG | 488.8341 | [9 empty] | Chlorine |  | 10267.9334 | 0.64175
Binney Cost per KG | 0.7949 |  | South Platte Cost per KG | 17.9502 |  | Aurora Reservoir Cost per KG | 0.48883 | 139.3929 | [8 empty] | Ferric Chloride |  | 13983.4905 | 3.6282
[17 empty] | Hydrogen Peroxide |  | 0 | 0
Notes: | [16 empty] | Potassium Permanganate |  | 6350.7541 | 0.49547
1. The difference between the "Binney MG Produced" and the Net numbers is the ammont of water needed from distribution to create the finished water (W3 to Chlorine and NaOH Motive) | [16 empty] | Sodium Hydroxide |  | 4982.5934 | 1.4221
Note on AF9: jamoore: Totals manually adjusted due to plant upset and waste to lagoon from finished water. Actual finished water flow less than net filter flows. Total finished water flow = 20.7549 MG. True net filter flow (gross to CCB): AR = 18.0MG, SP = 6.0MG.
Note on AG9: jamoore: Totals manually adjusted due to plant upset and waste to lagoon from finished water. Actual finished water flow less than net filter flows. Total finished water flow = 20.7549 MG. True net filter flow (gross to CCB): AR = 18.0MG, SP = 6.0MG.
Note on AH9: jamoore: Totals manually adjusted due to plant upset and waste to lagoon from finished water. Actual finished water flow less than net filter flows. Total finished water flow = 20.7549 MG. True net filter flow (gross to CCB): AR = 18.0MG, SP = 6.0MG.
Note on B40: Peter Bong: 3% Solution Strength
Note on C40: Peter Bong: 40% Solution Strength
Note on D40: Peter Bong: 50% Solution Strength
Note on E40: Peter Bong: 100% Solution Strength, PEC Cost
Note on F40: Peter Bong: 0.5% Solution Strength
Note on G40: Peter Bong: 99% Solution Strength
Note on H40: Peter Bong: 35% Solution Strength
Note on I40: Peter Bong: 3% Solution Strength
Note on J40: Peter Bong: 40% Solution Strength
Note on K40: Peter Bong: 100% Solution Strength
Note on L40: Peter Bong: 5.5% Solution Strength
Note on M40: Peter Bong: 0.5% Solution Strength
Note on N40: Peter Bong: 0.5% Solution Strength
Note on O40: Peter Bong: 100% Solution Strength
Note on P40: Peter Bong: 100% Solution Strength
Note on Q40: Peter Bong: 100% Solution Strength
Note on R40: Peter Bong: 100% Solution Strength
Note on S40: Peter Bong: 40% Solution Strength
Note on T40: Peter Bong: 40% Solution Strength
Note on U40: Peter Bong: 100% Solution Strength
Note on V40: Peter Bong: 100% Solution Strength
Note on Y40: Peter Bong: 50% Solution Strength
Note on Z40: Peter Bong: 50% Solution Strength
Note on AB40: Peter Bong: 100% Solution Strength
Note on AC40: Peter Bong: 3% Solution Strength
Note on AJ40: Peter Bong: Cost per kW*Hr
Note on AK40: Peter Bong: Cost per kW*Hr
Note on AL40: Peter Bong: Cost per kW*Hr
Note on AM40: Peter Bong: Cost per kW*Hr
Note on AN40: Peter Bong: Cost per kW*Hr
Note on AO40: Peter Bong: Cost per kW*Hr
Note on AP40: Peter Bong: Cost per kW*Hr
Note on AQ40: Peter Bong: Cost per kW*Hr
Note on AR40: Peter Bong: Cost per kW*Hr
Note on AS40: Peter Bong: Cost per kW*Hr
Note on AI42: Peter Bong: See Utility Summary Seet For Data

## DECEMBER
Current Application Point |  | Notes: Chemical are arranged in general process flow
Not in Use
[45 empty] | pass | bwpfcost
| South Platte | [6 empty] | Aurora Reservoir | [5 empty] | Filters/Adsorbers | [5 empty] | Finished Water | [6 empty] | From Chlorinator 5 | Valve Vault 1 (To Wemlinger RWAR) | RWAR Flow to Process | RWSP Flow to Process | Finished Water Flow | AR Net to Distribution | SP Net to Distribution | AR to Total Flow Blend | Blended&RW | Softening | Pre-Chem | Floc/Sed | UV/AOP | Filtration/Ad | Post-Chem | Finished | Recycle | Control
| KMnO4 (RW) | FeCl3 (Rapid Mix & Flow Split) | NaOH (Rapid Mix) | PEC/PEA (Reactors) | PEA (Sludge) | CO2 (Post Softening) | H202 (UV) | KMnO4 (RW) | FeCl3 (Rapid Mix) | PEC (Rapid Mix) | PAC (Basin 1 & 2) | PEA (Basin 1 & 2) | PEA (Sludge) | PEN AR (FIC) | PEN SP (FIC) | PEN AR (Individual Filters) | PEN SP (Individual Filters) | FeCl3 AR (Backwash Supply) | FeCl3 SP (Backwash Supply) | Cl2 AR | Cl2 SP | NH3 AR (CCB Effluent) | NH3 SP (CCB Effluent) | NaOH AR (CCB Effluent) | NaOH SP (CCB Effluent) | Fluoride(CCB Effluent) | Cl2 to RWAR, RWSP, ARFIC, or SPFIC | KMnO4 (RWAR to Wemlinger) |  |  | Total Produced From Binney
| Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Lbs per day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Gallons per Day | Lbs per day | Gallons per Day | MGD | MGD | MGD | MGD | MGD | Ratio | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day | kWxhrs per Day
2019-12-01 |  | 0 | 0 | 0 | 0 | 0 | 0 | 196.2991 | 424.2646 | 25.3274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261.9881 | 0 | 37.2433 | 0 | 149.7228 | 0 | 0 | 46.5431 | 0 | 10.4306 | 0 | 9.6993 | 9.5353 | 0 | 1 | 257.4564 | 597.0773 | 973.0247 | 546.13 | 1807.8726 | 1839.4429 | 1082.943 | 1929.6065 | 449.9688 | 537.6612
2019-12-02 |  | 0 | 0 | 0 | 0 | 0 | 0 | 196.0894 | 424.1538 | 25.3177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275.186 | 0 | 39.8481 | 0 | 158.3346 | 0 | 0 | 46.484 | 0 | 10.4271 | 0 | 10.2295 | 10.0003 | 0 | 1 | 241.8662 | 561.1634 | 964.0448 | 520.9052 | 1557.872 | 1730.7117 | 993.8101 | 1946.9581 | 429.8901 | 611.9013
2019-12-03 |  | 0 | 0 | 0 | 0 | 0 | 0 | 196.13 | 424.1692 | 25.5208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268.9833 | 0 | 38.3464 | 0 | 154.3718 | 0 | 0 | 46.4657 | 0 | 10.4263 | 0 | 9.9808 | 9.7416 | 0 | 1 | 238.1523 | 540.5388 | 918.8568 | 482.8483 | 1180.6308 | 1656.4106 | 592.217 | 1928.6766 | 438.1719 | 623.2531
2019-12-04 |  | 0 | 0 | 0 | 0 | 0 | 0 | 188.3589 | 423.744 | 25.5485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279.0204 | 0 | 39.84 | 0 | 157.2743 | 0 | 0 | 46.4696 | 0 | 10.4189 | 0 | 10.2222 | 10.0003 | 0 | 1 | 235.711 | 536.8114 | 940.7306 | 482.8483 | 1180.6308 | 1649.3622 | 590.6947 | 1926.1076 | 345.7586 | 663.0283
2019-12-05 |  | 0 | 0 | 0 | 0 | 0 | 0 | 192.3315 | 423.7655 | 25.5456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276.2883 | 0 | 39.6969 | 0 | 158.6668 | 0 | 0 | 46.4683 | 0 | 10.4198 | 0 | 10.0898 | 9.8688 | 0 | 1 | 251.5912 | 596.0985 | 1475.8628 | 482.8483 | 1180.6308 | 1698.7271 | 611.8122 | 1929.0678 | 341.5082 | 573.8832
2019-12-06 |  | 0 | 0 | 0 | 0 | 0 | 0 | 192.6805 | 424.4638 | 25.5087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271.6433 | 0 | 39.0604 | 0 | 157.4234 | 0 | 0 | 46.4675 | 0 | 10.4355 | 0 | 9.9144 | 9.676 | 0 | 1 | 259.9109 | 582.6749 | 2810.0713 | 482.8483 | 1180.6308 | 1701.0236 | 615.7504 | 1953.4847 | 348.475 | 593.6462
2019-12-07 |  | 0 | 0 | 0 | 0 | 0 | 0 | 193.98 | 427.5623 | 25.5958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275.0576 | 0 | 39.0477 | 0 | 160.563 | 0 | 0 | 47.1617 | 0 | 10.5089 | 0 | 10.0813 | 9.8348 | 0 | 1 | 245.3046 | 560.167 | 2774.8877 | 482.8483 | 1180.6308 | 1607.2203 | 589.012 | 1920.7527 | 346.4793 | 649.9942
2019-12-08 |  | 0 | 0 | 0 | 0 | 0 | 0 | 192.5165 | 424.355 | 25.3199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.1493 | 0 | 38.2077 | 0 | 158.1808 | 0 | 0 | 46.9779 | 0 | 10.431 | 0 | 9.971 | 9.7352 | 0 | 1 | 246.0148 | 561.2847 | 2749.7948 | 482.8483 | 1180.6308 | 1633.1409 | 580.6896 | 1907.8553 | 347.7302 | 630.3244
2019-12-09 |  | 41.4909 | 473.9931 | 10.9531 | 0 | 2689.0339 | 0 | 181.7371 | 424.1584 | 25.1783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271.0979 | 0 | 38.0656 | 0 | 156.5888 | 0 | 0 | 65.9781 | 0 | 10.4324 | 3.9373 | 9.9422 | 9.714 | 0 | 1 | 261.9423 | 829.7021 | 2735.3614 | 482.8483 | 1180.6308 | 1675.0379 | 597.1285 | 1936.8153 | 365.1282 | 586.5461
2019-12-10 |  | 68.391 | 765.3846 | 17.6073 | 0 | 4576.3996 | 15.8005 | 162.4451 | 385.0815 | 22.7369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.6934 | 51.7562 | 33.0411 | 6.7408 | 136.5336 | 27.8544 | 0 | 75.0964 | 0 | 9.4737 | 6.4537 | 10.2226 | 8.4027 | 1.7142 | 0.83056 | 270.0559 | 988.3329 | 2716.7437 | 482.8483 | 1180.6308 | 1909.0607 | 641.0415 | 2149.2988 | 370.7102 | 553.7556
2019-12-11 |  | 68.9046 | 785.7527 | 17.7683 | 0 | 3341.7078 | 27.0167 | 124.2162 | 262.9022 | 15.5999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172.2335 | 171.055 | 25.3453 | 25.1719 | 84.4273 | 83.8496 | 0 | 62.5961 | 0 | 6.8573 | 6.4585 | 12.2558 | 6.0761 | 6.0345 | 0.50172 | 258.9298 | 966.3027 | 2795.2732 | 482.8483 | 1180.6308 | 2242.7143 | 630.6692 | 2566.303 | 383.4593 | 592.5538
2019-12-12 |  | 69.2597 | 891.5538 | 17.7468 | 0 | 3905.4505 | 2.6213 | 204.2915 | 453.5749 | 27.1998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319.0404 | 34.2627 | 47.9512 | 5.1496 | 154.3763 | 16.5789 | 0 | 87.2348 | 0 | 12.2205 | 6.4693 | 12.7571 | 11.3641 | 1.2204 | 0.90302 | 256.471 | 959.2451 | 2902.3454 | 482.8483 | 1180.6308 | 1815.1567 | 620.4897 | 2401.7385 | 378.4787 | 633.0108
2019-12-13 |  | 69.6415 | 936.5606 | 17.7691 | 0 | 3726.471 | 16.8436 | 161.1541 | 367.457 | 21.3012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248.3073 | 103.4949 | 37.2547 | 15.5278 | 132.2175 | 55.1084 | 0 | 75.1256 | 0 | 9.5691 | 6.4571 | 12.87 | 8.9782 | 3.7421 | 0.70582 | 266.5947 | 974.2273 | 2888.2483 | 482.8483 | 1180.6308 | 2044.0059 | 631.2636 | 2141.948 | 381.5362 | 609.7902
2019-12-14 |  | 69.251 | 949.7502 | 17.9322 | 0 | 4643.3673 | 25.843 | 121.5008 | 254.7865 | 14.8112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174.7521 | 174.696 | 26.3816 | 26.3731 | 93.2506 | 93.2207 | 0 | 63.109 | 0 | 6.8667 | 6.4569 | 12.9819 | 6.4128 | 6.4107 | 0.50008 | 270.2871 | 977.686 | 3006.7577 | 482.8483 | 1180.6308 | 2510.0471 | 652.0709 | 2126.0421 | 409.5003 | 530.1986
2019-12-15 |  | 69.1155 | 968.9571 | 17.7906 | 0 | 4622.4804 | 25.9659 | 121.1403 | 254.2214 | 14.7905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.9843 | 165.9019 | 25.9646 | 25.0463 | 90.9966 | 87.7784 | 0 | 63.1083 | 0 | 6.8513 | 6.4668 | 12.5163 | 6.2956 | 6.073 | 0.509 | 275.8417 | 1002.6031 | 2775.9402 | 482.8483 | 1180.6308 | 2598.1645 | 684.7443 | 2100.2132 | 415.8272 | 564.3203
2019-12-16 |  | 61.085 | 906.8052 | 15.6085 | 0 | 4352.3705 | 22.6412 | 137.8183 | 287.8616 | 17.1185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.8404 | 149.9258 | 29.399 | 22.7387 | 108.792 | 84.1451 | 0 | 62.5061 | 0 | 7.7598 | 5.6455 | 12.8072 | 7.0385 | 5.4439 | 0.56387 | 285.3878 | 1014.3272 | 2855.7728 | 482.8483 | 1180.6308 | 2569.104 | 673.9237 | 2232.4053 | 436.8224 | 580.9333
2019-12-17 |  | 16.4009 | 255.4339 | 4.708 | 0 | 1949.2574 | 6.5975 | 168.408 | 359.6484 | 21.5556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254.1593 | 41.0575 | 37.6076 | 6.0752 | 139.3585 | 22.5123 | 0 | 50.9897 | 0 | 9.6924 | 1.5581 | 10.7814 | 9.2556 | 1.4952 | 0.86092 | 287.3127 | 1009.5359 | 2830.3523 | 481.5387 | 3089.0072 | 1959.9693 | 675.9021 | 2002.9057 | 391.2287 | 661.4303
2019-12-18 |  | 0 | 0 | 0 | 0 | 0 | 0 | 177.9244 | 383.3536 | 23.2044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281.5726 | 0 | 38.9283 | 0 | 147.5782 | 0 | 0 | 46.4587 | 0 | 10.3281 | 0 | 10.1609 | 9.9993 | 0 | 1 | 265.2354 | 951.8994 | 2799.4505 | 480.9386 | 3704.1354 | 1626.614 | 610.0334 | 1950.6636 | 345.3391 | 634.9172
2019-12-19 |  | 22.7478 | 328.1453 | 6.0525 | 0 | 1674.4053 | 0 | 179.4747 | 382.1764 | 23.4229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282.5607 | 0 | 39.7733 | 0 | 143.1296 | 0 | 0 | 57.5635 | 0 | 10.4201 | 2.1524 | 9.9828 | 9.8271 | 0 | 1 | 262.0818 | 941.7788 | 2703.5411 | 480.9386 | 3704.1354 | 1669.4775 | 595.638 | 1936.4507 | 342.4599 | 599.2651
2019-12-20 |  | 63.8527 | 892.354 | 16.3707 | 0 | 4052.2257 | 15.8956 | 178.1627 | 433.5499 | 25.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286.3877 | 87.3613 | 44.9611 | 13.7152 | 167.2569 | 51.0209 | 0 | 82.448 | 0 | 11.6861 | 5.9647 | 14.1677 | 10.8533 | 3.3108 | 0.76626 | 266.7437 | 975.2554 | 2791.4107 | 480.9386 | 3704.1354 | 2237.2929 | 616.7608 | 2354.6645 | 365.5229 | 570.1004
2019-12-21 |  | 63.9879 | 944.9665 | 16.3166 | 0 | 3593.383 | 23.9923 | 162.7505 | 514.6707 | 31.0414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325.9403 | 144.9336 | 51.7687 | 23.0196 | 207.8036 | 92.4026 | 0 | 92.657 | 0 | 13.8665 | 5.9694 | 19.3727 | 13.2841 | 5.9069 | 0.6922 | 251.0981 | 960.7885 | 2729.3434 | 480.9386 | 3704.1354 | 2509.714 | 579.6945 | 2559.4747 | 367.4983 | 625.2337
2019-12-22 |  | 62.8688 | 937.9533 | 16.4388 | 0 | 3263.7796 | 24.0634 | 142.2427 | 384.3736 | 22.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258.3076 | 154.9624 | 39.1036 | 23.4588 | 157.4636 | 94.4646 | 0 | 77.587 | 0 | 10.359 | 5.9696 | 16.1757 | 9.9998 | 5.999 | 0.62503 | 242.3496 | 936.6594 | 2716.8274 | 480.9386 | 3704.1354 | 2485.8633 | 558.0323 | 2135.4682 | 342.3203 | 657.2971
2019-12-23 |  | 62.86 | 946.1523 | 16.511 | 0 | 3239.0922 | 24.03 | 144.1603 | 384.31 | 22.7756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.5763 | 158.1179 | 40.0243 | 24.0104 | 153.054 | 91.8162 | 0 | 77.7687 | 0 | 10.3576 | 5.9779 | 15.731 | 9.7186 | 5.8302 | 0.62504 | 238.8344 | 935.5232 | 2979.9415 | 480.9386 | 3704.1354 | 2497.2285 | 572.2024 | 2126.8257 | 341.6894 | 651.3439
2019-12-24 |  | 62.446 | 953.4019 | 16.6517 | 0 | 3422.9475 | 23.862 | 144.0438 | 384.3967 | 22.8001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262.1762 | 151.0795 | 39.9194 | 23.0036 | 156.1397 | 89.9758 | 0 | 76.2756 | 0 | 10.3591 | 5.9521 | 15.8069 | 9.9094 | 5.7103 | 0.63442 | 249.0319 | 942.4596 | 2751.1795 | 480.9386 | 3704.1354 | 2489.9413 | 587.0433 | 2117.8172 | 357.752 | 600.2737
2019-12-25 |  | 63.157 | 963.1357 | 16.7594 | 0 | 3896.9717 | 23.9681 | 143.9319 | 384.2846 | 22.783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262.3339 | 157.412 | 39.6663 | 23.8016 | 154.4509 | 92.6774 | 0 | 76.3521 | 0 | 10.3564 | 5.9851 | 16.0376 | 9.9152 | 5.9495 | 0.62498 | 253.327 | 944.2675 | 2829.7912 | 480.9386 | 3704.1354 | 2482.2381 | 597.5724 | 2171.574 | 366.3049 | 530.1259
2019-12-26 |  | 62.8655 | 964.1686 | 16.6465 | 0 | 4278.5823 | 24.0853 | 144.2752 | 384.4081 | 22.7396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260.6523 | 156.334 | 40.0544 | 24.0238 | 150.0893 | 90.0205 | 0 | 76.3553 | 0 | 10.3597 | 5.9923 | 15.9414 | 9.8556 | 5.9112 | 0.62509 | 259.1568 | 955.4202 | 2708.2807 | 480.9386 | 3704.1354 | 2530.7808 | 617.6584 | 2180.3538 | 384.7291 | 570.814
2019-12-27 |  | 64.0583 | 968.8381 | 16.9896 | 0 | 4425.2612 | 24.1081 | 144.2056 | 384.4603 | 22.6949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.9586 | 147.0857 | 39.0326 | 22.6066 | 147.5324 | 85.4466 | 0 | 77.5477 | 0 | 10.3599 | 6.0205 | 15.4359 | 9.6621 | 5.596 | 0.63324 | 264.7466 | 973.643 | 2707.092 | 480.9386 | 3704.1354 | 2569.7696 | 587.7378 | 2171.4053 | 401.9225 | 618.2702
2019-12-28 |  | 63.8791 | 973.2154 | 16.7501 | 0 | 4605.175 | 24.2129 | 145.6868 | 388.8101 | 22.9641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254.178 | 151.9863 | 39.6619 | 23.7159 | 150.0072 | 89.6972 | 0 | 77.567 | 0 | 10.4785 | 6.0485 | 15.8739 | 9.8246 | 5.8746 | 0.6258 | 292.6385 | 1028.0727 | 2763.8396 | 480.9386 | 3704.1354 | 2547.703 | 678.9044 | 2156.4998 | 435.7813 | 586.6431
2019-12-29 |  | 63.6807 | 961.2199 | 16.6198 | 0 | 4656.0457 | 24.2289 | 150.3475 | 389.5111 | 23.0236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251.4433 | 150.8003 | 40.482 | 24.2786 | 151.7784 | 91.0274 | 0 | 77.9107 | 0 | 10.4971 | 6.0387 | 16.081 | 9.9044 | 5.94 | 0.6251 | 289.6445 | 1028.4864 | 2781.726 | 480.9386 | 3704.1354 | 2668.3701 | 1102.3164 | 2157.7385 | 438.7545 | 554.437
2019-12-30 |  | 64.0585 | 946.7883 | 16.3588 | 0 | 4561.3653 | 24.1245 | 151.4954 | 387.7354 | 22.9079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.6076 | 144.2839 | 39.914 | 23.3527 | 149.9021 | 87.704 | 0 | 77.7578 | 0 | 10.4491 | 6.0314 | 15.7823 | 9.7945 | 5.7305 | 0.63089 | 285.5398 | 1030.0989 | 2816.8335 | 480.9386 | 3704.1354 | 2579.7798 | 920.0311 | 2113.07 | 427.5868 | 606.3427
2019-12-31 |  | 63.9113 | 944.0601 | 16.2714 | 0 | 4511.5362 | 24.1008 | 151.1212 | 387.559 | 22.9408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249.2012 | 149.4686 | 39.7542 | 23.8442 | 151.6631 | 90.9661 | 0 | 77.7673 | 0 | 10.4446 | 6.0139 | 16.1161 | 9.9187 | 5.9492 | 0.62508 | 276.1454 | 1009.4147 | 2810.0824 | 480.9386 | 3704.1354 | 2559.3043 | 991.5063 | 2116.5549 | 401.9746 | 640.0516
Monthly Chemical/Power Usage | 0 | 1317.9139 | 18658.5907 | 342.6208 | 0 | 83987.3091 | 424.0015 | 5090.9198 | 12019.7697 | 715.9596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7979.3213 | 2645.9753 | 1185.3453 | 405.6543 | 4538.9278 | 1518.2672 | 0 | 2030.7986 | 0 | Total MG | Total MG | Total MG | Total MG | Total MG | Overall Ratio | 8105.4039 | 26871.5459 | 78003.4082 | 15041.5897 | 74841.4786 | 66293.3771 | 21079.2938 | 65348.7401 | 11900.3089 | 18641.3466
Cost per Gallon or lb or kW*Hr | 0.82128 | 1.4864 | 2.954 | 4.3368 | 0 | 0.059975 | 3.739 | 0.82128 | 1.4864 | 4.3368 | 0 | 0 | 0 | 15.77 | 15.77 | 15.77 | 15.77 | 1.4864 | 1.4864 | 0.2996 | 0.2996 | 0.74349 | 0.74349 | 2.954 | 2.954 | 0 | 0.2996 | 0.82128 | 313.543 | 124.0197 | 399.989 | 294.3965 | 99.8424 | 0.74675 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067
Cost Per Month | 0 | 1958.8876 | 55117.9993 | 1485.8779 | 0 | 5037.1389 | 1585.3547 | 4181.091 | 17865.6424 | 3104.9736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2390.6047 | 792.7342 | 881.2975 | 301.6017 | 13408.1197 | 4485.0039 | 0 | 608.4272 | 0 | [6 empty] | 543.0621 | 1800.3936 | 5226.2284 | 1007.7865 | 5014.3791 | 4441.6563 | 1412.3127 | 4378.3656 | 797.3207 | 1248.9702
2019-12-02 | [33 empty] | Natural Gas | 1297.94 | NA | 2213.93 | 808.31 | 1536.17 | 6286.15 | 1921.67 | NA | 245.14 | 445.55
Total Binney WPF Costs |  |  | South Platte Costs |  |  | Aurora Reservoir Costs |  |  | Labor Costs | [7 empty] | Monthly Truck Loads
Chemical | 113204.7542 |  | Chemical | 70764.5981 |  | Chemical | 41831.7289 |  | Monthly | 280358.29 | [6 empty] | Chemical |  | Gallon/Lbs | Loads
Electrical | 25870.475 |  | Electrical | 13179.9393 |  | Electrical | 12690.5357 | [9 empty] | Ammonia |  | 1590.9996 | 0.43984
Natural Gas | 14754.86 |  | Natural Gas | 5395.8471 |  | Natural Gas | 9359.0129 |  | Material Costs | [7 empty] | Anionic Polymer |  | 0 | 0
Labor | 280358.29 |  | Labor | 140179.145 |  | Labor | 140179.145 |  | Monthly | 74794.6 | [6 empty] | Carbon Dioxide |  | 83987.3091 | 2.0997
Materials | 74794.6 |  | Materials | 37397.3 |  | Materials | 37397.3 | [9 empty] | Carbon PAC |  | 0 | 0
Binney MG Produced | 399.989 |  | Net South Platte MG Produced | 99.8424 |  | Net Aurora Reservoir MG Produced | 294.3965 | [9 empty] | Cationic Polymer |  | 1058.5804 | 0.20404
Total Treated (MG) | 437.5627 |  | RWSP to Process (MG) | 124.0197 |  | RWAR to Process | 313.543
Binney Cost per MG | 1163.2228 |  | South Platte Cost per MG | 2152.2127 | 570.5915 | Aurora Reservoir Cost per MG | 770.0944 | 133.4162 | [8 empty] | Chlorine |  | 12656.0952 | 0.79101
Binney Cost per KG | 1.1632 |  | South Platte Cost per KG | 2.1522 |  | Aurora Reservoir Cost per KG | 0.77009 | [9 empty] | Ferric Chloride |  | 13337.6836 | 3.4607
[17 empty] | Hydrogen Peroxide |  | 424.0015 | 0.08919
Notes: | [16 empty] | Potassium Permanganate |  | 5090.9198 | 0.39718
1. The difference between the "Binney MG Produced" and the Net numbers is the ammont of water needed from distribution to create the finished water (W3 to Chlorine and NaOH Motive) | [16 empty] | Sodium Hydroxide |  | 24715.7857 | 7.0542
Note on B40: Peter Bong: 3% Solution Strength
Note on C40: Peter Bong: 40% Solution Strength
Note on D40: Peter Bong: 50% Solution Strength
Note on E40: Peter Bong: 100% Solution Strength, PEC Cost
Note on F40: Peter Bong: 0.5% Solution Strength
Note on G40: Peter Bong: 99% Solution Strength
Note on H40: Peter Bong: 35% Solution Strength
Note on I40: Peter Bong: 3% Solution Strength
Note on J40: Peter Bong: 40% Solution Strength
Note on K40: Peter Bong: 100% Solution Strength
Note on L40: Peter Bong: 5.5% Solution Strength
Note on M40: Peter Bong: 0.5% Solution Strength
Note on N40: Peter Bong: 0.5% Solution Strength
Note on O40: Peter Bong: 100% Solution Strength
Note on P40: Peter Bong: 100% Solution Strength
Note on Q40: Peter Bong: 100% Solution Strength
Note on R40: Peter Bong: 100% Solution Strength
Note on S40: Peter Bong: 40% Solution Strength
Note on T40: Peter Bong: 40% Solution Strength
Note on U40: Peter Bong: 100% Solution Strength
Note on V40: Peter Bong: 100% Solution Strength
Note on Y40: Peter Bong: 50% Solution Strength
Note on Z40: Peter Bong: 50% Solution Strength
Note on AB40: Peter Bong: 100% Solution Strength
Note on AC40: Peter Bong: 3% Solution Strength
Note on AJ40: Peter Bong: Cost per kW*Hr
Note on AK40: Peter Bong: Cost per kW*Hr
Note on AL40: Peter Bong: Cost per kW*Hr
Note on AM40: Peter Bong: Cost per kW*Hr
Note on AN40: Peter Bong: Cost per kW*Hr
Note on AO40: Peter Bong: Cost per kW*Hr
Note on AP40: Peter Bong: Cost per kW*Hr
Note on AQ40: Peter Bong: Cost per kW*Hr
Note on AR40: Peter Bong: Cost per kW*Hr
Note on AS40: Peter Bong: Cost per kW*Hr
Note on AI42: Peter Bong: See Utility Summary Seet For Data