## chem
Month | 2022-04-01
Date | gal ortho | gal NAOH | GAL FLUR | lbs ortho | lbs NAOH | lbs Fluor | gal/hr PAC | lbs/day PAC | gal/hr poly | lbs/day poly | O3 lb/day | CL2 lb/day | kmno4 gal/hr | kmno4lbs/day | DATE
1 | 7 | 46.2 | 7 | 71.75 | 134.1648 | 16.177 | 2.14 | 529.008 | 15 | 5.9724 | 31.22 | 28.82 | 0 | 0 | 1
2 | 8 | 46.65 | 7 | 82 | 135.4716 | 16.177 | 1.95 | 482.04 | 15 | 5.9724 | 30.63 | 28.3 | 0 | 0 | 2
3 | 7.5 | 44.4 | 7.5 | 76.875 | 128.9376 | 17.3325 | 1.92 | 474.624 | 15 | 5.9724 | 30.72 | 27.31 | 0 | 0 | 3
4 | 8 | 42.6 | 7 | 82 | 123.7104 | 16.177 | 2.18 | 538.896 | 15 | 5.9724 | 30.44 | 27.48 | 0 | 0 | 4
5 | 8 | 44.85 | 7.5 | 82 | 130.2444 | 17.3325 | 1.9 | 469.68 | 15.5 | 6.1715 | 31.97 | 29.44 | 0 | 0 | 5
6 | 8 | 44.6 | 8 | 82 | 129.5184 | 18.488 | 2.36 | 583.392 | 14.8 | 5.8928 | 30.69 | 29.87 | 0 | 0 | 6
7 | 8 | 45.1 | 7.5 | 82 | 130.9704 | 17.3325 | 2.02 | 499.344 | 14.6 | 5.8131 | 31.15 | 29 | 0 | 0 | 7
8 | 8 | 47.7 | 7.5 | 82 | 138.5208 | 17.3325 | 1.85 | 457.32 | 14.6 | 5.8131 | 34.07 | 30.96 | 0 | 0 | 8
9 | 8 | 46.2 | 7.5 | 82 | 134.1648 | 17.3325 | 1.73 | 427.656 | 14.6 | 5.8131 | 33.82 | 31.76 | 0 | 0 | 9
10 | 7.5 | 45.3 | 7 | 76.875 | 131.5512 | 16.177 | 1.56 | 385.632 | 14.6 | 5.8131 | 33.19 | 28.24 | 0 | 0 | 10
11 | 7.5 | 44.7 | 7.5 | 76.875 | 129.8088 | 17.3325 | 1.55 | 383.16 | 14.6 | 5.8131 | 33.36 | 28.01 | 0 | 0 | 11
12 | 7 | 43.1 | 7.5 | 71.75 | 125.1624 | 17.3325 | 1.5 | 370.8 | 14 | 5.5742 | 32.16 | 24.73 | 0 | 0 | 12
13 | 8 | 45 | 8 | 82 | 130.68 | 18.488 | 1.7 | 420.24 | 14.5 | 5.7733 | 33.32 | 28.09 | 0 | 0 | 13
14 | 9 | 50.4 | 9 | 92.25 | 146.3616 | 20.799 | 2.17 | 536.424 | 14.5 | 5.7733 | 34.18 | 30 | 0 | 0 | 14
15 | 8 | 43.2 | 8 | 82 | 125.4528 | 18.488 | 1.72 | 425.184 | 14.5 | 5.7733 | 33.53 | 26 | 0 | 0 | 15
16 | 8 | 43.9 | 9 | 82 | 127.4856 | 20.799 | 1.56 | 385.632 | 14.5 | 5.7733 | 31.33 | 24.19 | 0 | 0 | 16
17 | 8 | 46.2 | 9 | 82 | 134.1648 | 20.799 | 1.71 | 422.712 | 14.5 | 5.7733 | 30.32 | 25.83 | 0 | 0 | 17
18 | 9 | 49.95 | 9 | 92.25 | 145.0548 | 20.799 | 2.3 | 568.56 | 14.6 | 5.8131 | 30.27 | 28.43 | 0 | 0 | 18
19 | 7.5 | 45.9 | 7.5 | 76.875 | 133.2936 | 17.3325 | 1.66 | 410.352 | 14.6 | 5.8131 | 29.72 | 24.9 | 0 | 0 | 19
20 | 9 | 51.3 | 8.5 | 92.25 | 148.9752 | 19.6435 | 2.61 | 645.192 | 14.5 | 5.7733 | 32.44 | 26.05 | 0 | 0 | 20
21 | 8 | 47.7 | 9 | 82 | 138.5208 | 20.799 | 2.82 | 697.104 | 14.9 | 5.9326 | 37.9 | 29.45 | 0 | 0 | 21
22 | 9 | 49.2 | 9 | 92.25 | 142.8768 | 20.799 | 2.59 | 640.248 | 14.7 | 5.853 | 33.22 | 28.51 | 0 | 0 | 22
23 | 9 | 48.45 | 9 | 92.25 | 140.6988 | 20.799 | 1.81 | 1437 | 14.7 | 5.853 | 34.77 | 25.73 | 0 | 0 | 23
24 | 8 | 48 | 8 | 82 | 139.392 | 18.488 | 1.95 | 482.04 | 14.7 | 5.853 | 34.93 | 26.09 | 0 | 0 | 24
25 | 8 | 44.8 | 9 | 82 | 130.0992 | 20.799 | 2.32 | 573.504 | 14.9 | 5.9326 | 38.23 | 29.35 | 0 | 0 | 25
26 | 9 | 56.6 | 10 | 92.25 | 164.3664 | 23.11 | 5.94 | 1468.368 | 13.8 | 5.4946 | 35.32 | 27.55 | 0 | 0 | 26
27 | 9 | 53.6 | 10 | 92.25 | 155.6544 | 23.11 | 2.33 | 575.976 | 15.2 | 6.052 | 36.81 | 29.6 | 0 | 0 | 27
28 | 9.5 | 55.5 | 9 | 97.375 | 161.172 | 20.799 | 1.94 | 479.568 | 15.2 | 6.052 | 33.56 | 28.28 | 0 | 0 | 28
29 | 9.5 | 54 | 7 | 97.375 | 156.816 | 16.177 | 2.86 | 706.992 | 15.2 | 6.052 | 37.74 | 35.6 | 0 | 0 | 29
30 | 7 | 54 | 9.5 | 71.75 | 156.816 | 21.9545 | 2.25 | 556.2 | 15.2 | 6.052 | 36.14 | 32.3 | 0 | 0 | 30
31
Tot | 245 | 1429.1 | 246 | 2511.25 | 4150.1064 | 568.506 | 64.9 | 16043.28 | 442 | 175.9867 | 997.15 | 849.87 | 0 | 0 | Total
AVG | 8.1667 | 47.6367 | 8.2 | 83.7083 | 138.3369 | 18.9502 | 2.1633 | 534.776 | 14.7333 | 5.8662 | 33.2383 | 28.329 | 0 | 0 | Avg.
Date | Raw Water | Post NAOH | Corrosion | Flouride | Chlorine | PACL | KmnO4 | Polymer | Ozone | Raw Water | Raw Water | Pump
| /1,000 gal | lbs/day | Inhibitor | lbs/day | lbs/day | lbs/day | lbs/day | lbs/day | lbs/day | Temp oF | Turbidity | Station
|  |  | lbs/day | [8 empty] | pH
1 | 2592 | 134.1648 | 71.75 | 16.177 | 28.82 | 529.008 | 0 | 5.9724 | 31.22 | 44.98 | 2.83 | 7.6
2 | 2513 | 135.4716 | 82 | 16.177 | 28.3 | 482.04 | 0 | 5.9724 | 30.63 | 44.47 | 2.77 | 7.7
3 | 2488 | 128.9376 | 76.875 | 17.3325 | 27.31 | 474.624 | 0 | 5.9724 | 30.72 | 44.17 | 2.79 | 7.6
4 | 2442 | 123.7104 | 82 | 16.177 | 27.48 | 538.896 | 0 | 5.9724 | 30.44 | 43.88 | 2.66 | 7.5
5 | 2173 | 130.2444 | 82 | 17.3325 | 29.44 | 469.68 | 0 | 6.1715 | 31.97 | 44.44 | 2.7 | 7.4
6 | 2683 | 129.5184 | 82 | 18.488 | 29.87 | 583.392 | 0 | 5.8928 | 30.69 | 45.41 | 2.86 | 7.4
7 | 2074 | 130.9704 | 82 | 17.3325 | 29 | 499.344 | 0 | 5.8131 | 31.15 | 46 | 2.82 | 7.5
8 | 2511 | 138.5208 | 82 | 17.3325 | 30.96 | 457.32 | 0 | 5.8131 | 34.07 | 46.41 | 3.01 | 7.5
9 | 2520 | 134.1648 | 82 | 17.3325 | 31.76 | 427.656 | 0 | 5.8131 | 33.82 | 46.09 | 3.19 | 7.6
10 | 2953 | 131.5512 | 76.875 | 16.177 | 28.24 | 385.632 | 0 | 5.8131 | 33.19 | 45 | 2.68 | 7.7
11 | 2363 | 129.8088 | 76.875 | 17.3325 | 28.01 | 383.16 | 0 | 5.8131 | 33.36 | 44.81 | 2.44 | 7.7
12 | 2226 | 125.1624 | 71.75 | 17.3325 | 24.73 | 370.8 | 0 | 5.5742 | 32.16 | 45.36 | 2.71 | 7.6
13 | 2425 | 130.68 | 82 | 18.488 | 28.09 | 420.24 | 0 | 5.7733 | 33.32 | 45.86 | 4.11 | 7.6
14 | 2105 | 146.3616 | 92.25 | 20.799 | 30 | 536.424 | 0 | 5.7733 | 34.18 | 46.93 | 3.9 | 7.5
15 | 2636 | 125.4528 | 82 | 18.488 | 26 | 425.184 | 0 | 5.7733 | 33.53 | 46.1 | 2.71 | 7.5
16 | 2440 | 127.4856 | 82 | 20.799 | 24.19 | 385.632 | 0 | 5.7733 | 31.33 | 45.74 | 2.2 | 7.5
17 | 2961 | 134.1648 | 82 | 20.799 | 25.83 | 422.712 | 0 | 5.7733 | 30.32 | 44.77 | 1.95 | 7.5
18 | 2806 | 145.0548 | 92.25 | 20.799 | 28.43 | 568.56 | 0 | 5.8131 | 30.27 | 44.82 | 3.14 | 7.5
19 | 2507 | 133.2936 | 76.875 | 17.3325 | 24.9 | 410.352 | 0 | 5.8131 | 29.72 | 45.11 | 3.18 | 7.7
20 | 2029 | 148.9752 | 92.25 | 19.6435 | 26.05 | 645.192 | 0 | 5.7733 | 32.44 | 45.33 | 3.16 | 7.6
21 | 2990 | 138.5208 | 82 | 20.799 | 29.45 | 697.104 | 0 | 5.9326 | 37.9 | 45.09 | 2.3 | 7.4
22 | 2657 | 142.8768 | 92.25 | 20.799 | 28.51 | 640.248 | 0 | 5.853 | 33.22 | 45.52 | 2.12 | 7.5
23 | 3226 | 140.6988 | 92.25 | 20.799 | 25.73 | 1437 | 0 | 5.853 | 34.77 | 45.96 | 1.87 | 7.5
24 | 2638 | 139.392 | 82 | 18.488 | 26.09 | 482.04 | 0 | 5.853 | 34.93 | 47.09 | 1.7 | 7.5
25 | 2890 | 130.0992 | 82 | 20.799 | 29.35 | 573.504 | 0 | 5.9326 | 38.23 | 47.38 | 1.57 | 7.5
26 | 2751 | 164.3664 | 92.25 | 23.11 | 27.55 | 1468.368 | 0 | 5.4946 | 35.32 | 47 | 1.55 | 7.5
27 | 2353 | 155.6544 | 92.25 | 23.11 | 29.6 | 575.976 | 0 | 6.052 | 36.81 | 46.07 | 1.65 | 7.5
28 | 2719 | 161.172 | 97.375 | 20.799 | 28.28 | 479.568 | 0 | 6.052 | 33.56 | 46.2 | 2.05 | 7.6
29 | 2932 | 156.816 | 97.375 | 16.177 | 35.6 | 706.992 | 0 | 6.052 | 37.74 | 46.55 | 1.88 | 7.6
30 | 2913 | 156.816 | 71.75 | 21.9545 | 32.3 | 556.2 | 0 | 6.052 | 36.14 | 46.67 | 1.87 | 7.6
31
TOT | 77516 | 4150.1064 | 2511.25 | 568.506 | 849.87 | 17032.848 | 0 | 175.9867 | 997.15 | 1369.21 | 76.37 | 226.4
AVG | 2583.8667 | 138.3369 | 83.7083 | 18.9502 | 28.329 | 567.7616 | 0 | 5.8662 |  | 1324.23 | 73.54 | 218.8

## filtr turb
2022-04-01
COMBINED FILTER TURBIDITY
Date | Filter | Filter | Filter | Filter | Filter | Filter | Average
| Turbidity | Turbidity | Turbidity | Turbidity | Turbidity | Turbidity | Daily
| 12:00 A.M. | 4:00 A.M. | 8:00 A.M. | 12:00 P.M. | 4:00 P.M. | 8:00 P.M. | Turbidity
1 | 0.025 | 0.027 | 0.034 | 0.024 | 0.027 | 0.027 | 0.027333
2 | 0.026 | 0.026 | 0.027 | 0.035 | 0.031 | 0.024 | 0.028167
3 | 0.022 | 0.023 | 0.025 | 0.026 | 0.02 | 0.025 | 0.0235
4 | 0.024 | 0.027 | 0.026 | 0.026 | 0.024 | 0.028 | 0.025833
5 | 0.027 | 0.029 | 0.028 | 0.024 | 0.026 | 0.025 | 0.0265
6 | 0.024 | 0.029 | 0.024 | 0.027 | 0.03 | 0.026 | 0.026667
7 | 0.023 | 0.029 | 0.028 | 0.029 | 0.028 | 0.031 | 0.028
8 | 0.034 | 0.031 | 0.025 | 0.028 | 0.032 | 0.035 | 0.030833
9 | 0.032 | 0.037 | 0.031 | 0.023 | 0.032 | 0.035 | 0.031667
10 | 0.029 | 0.034 | 0.025 | 0.029 | 0.018 | 0.029 | 0.027333
11 | 0.024 | 0.027 | 0.028 | 0.031 | 0.024 | 0.027 | 0.026833
12 | 0.024 | 0.019 | 0.027 | 0.019 | 0.029 | 0.023 | 0.0235
13 | 0.027 | 0.022 | 0.023 | 0.025 | 0.028 | 0.029 | 0.025667
14 | 0.027 | 0.029 | 0.035 | 0.038 | 0.036 | 0.035 | 0.033333
15 | 0.036 | 0.034 | 0.036 | 0.024 | 0.023 | 0.03 | 0.0305
16 | 0.035 | 0.025 | 0.034 | 0.035 | 0.033 | 0.031 | 0.032167
17 | 0.037 | 0.034 | 0.032 | 0.032 | 0.032 | 0.029 | 0.032667
18 | 0.029 | 0.03 | 0.035 | 0.024 | 0.033 | 0.03 | 0.030167
19 | 0.031 | 0.034 | 0.029 | 0.022 | 0.024 | 0.029 | 0.028167
20 | 0.03 | 0.027 | 0.028 | 0.028 | 0.025 | 0.027 | 0.0275
21 | 0.029 | 0.028 | 0.033 | 0.033 | 0.032 | 0.035 | 0.031667
22 | 0.013 | 0.028 | 0.034 | 0.036 | 0.029 | 0.033 | 0.028833
23 | 0.035 | 0.035 | 0.026 | 0.026 | 0.025 | 0.024 | 0.0285
24 | 0.029 | 0.03 | 0.029 | 0.028 | 0.023 | 0.024 | 0.027167
25 | 0.024 | 0.027 | 0.022 | 0.027 | 0.029 | 0.027 | 0.026
26 | 0.027 | 0.028 | 0.025 | 0.028 | 0.028 | 0.029 | 0.0275
27 | 0.019 | 0.022 | 0.023 | 0.028 | 0.029 | 0.025 | 0.024333
28 | 0.036 | 0.036 | 0.026 | 0.032 | 0.024 | 0.03 | 0.030667
29 | 0.031 | 0.026 | 0.025 | 0.024 | 0.03 | 0.035 | 0.0285
30 | 0.031 | 0.034 | 0.034 | 0.028 | 0.039 | 0.037 | 0.033833
31
All results are in NTU's
[6 empty] | MIN. | 0.0235
[6 empty] | MAX. | 0.033833
[6 empty] | AVG. | 0.028494

## entryturb
2022-04-01
ENTRY POINT TURBIDITY
Date | Entry Pt. | Entry Pt. | Entry Pt. | Entry Pt. | Entry Pt. | Entry Pt. | AVERAGE
| Turbidity | Turbidity | Turbidity | Turbidity | Turbidity | Turbidity | DAILY
| 12:00 A.M. | 4:00 A.M. | 8:00 A.M. | 12:00 P.M. | 4:00 P.M. | 8:00 P.M. | TURBIDITY
1 | 0.024 | 0.036 | 0.031 | 0.035 | 0.023 | 0.028 | 0.0295
2 | 0.023 | 0.025 | 0.028 | 0.02 | 0.029 | 0.022 | 0.0245
3 | 0.029 | 0.029 | 0.028 | 0.025 | 0.022 | 0.024 | 0.026167
4 | 0.025 | 0.028 | 0.021 | 0.024 | 0.037 | 0.027 | 0.027
5 | 0.029 | 0.029 | 0.027 | 0.027 | 0.036 | 0.029 | 0.0295
6 | 0.027 | 0.026 | 0.026 | 0.032 | 0.038 | 0.029 | 0.029667
7 | 0.024 | 0.027 | 0.03 | 0.03 | 0.026 | 0.025 | 0.027
8 | 0.035 | 0.042 | 0.028 | 0.029 | 0.041 | 0.041 | 0.036
9 | 0.045 | 0.045 | 0.032 | 0.029 | 0.025 | 0.035 | 0.035167
10 | 0.037 | 0.034 | 0.027 | 0.026 | 0.018 | 0.017 | 0.0265
11 | 0.019 | 0.019 | 0.023 | 0.032 | 0.027 | 0.027 | 0.0245
12 | 0.026 | 0.027 | 0.024 | 0.024 | 0.018 | 0.019 | 0.023
13 | 0.02 | 0.025 | 0.027 | 0.031 | 0.031 | 0.024 | 0.026333
14 | 0.03 | 0.027 | 0.033 | 0.034 | 0.037 | 0.044 | 0.034167
15 | 0.049 | 0.041 | 0.025 | 0.029 | 0.028 | 0.036 | 0.034667
16 | 0.047 | 0.037 | 0.032 | 0.036 | 0.035 | 0.035 | 0.037
17 | 0.035 | 0.031 | 0.042 | 0.057 | 0.048 | 0.035 | 0.041333
18 | 0.03 | 0.032 | 0.038 | 0.026 | 0.02 | 0.02 | 0.027667
19 | 0.031 | 0.029 | 0.034 | 0.04 | 0.046 | 0.03 | 0.035
20 | 0.029 | 0.032 | 0.025 | 0.028 | 0.027 | 0.025 | 0.027667
21 | 0.039 | 0.033 | 0.034 | 0.038 | 0.033 | 0.028 | 0.034167
22 | 0.025 | 0.025 | 0.031 | 0.03 | 0.031 | 0.035 | 0.0295
23 | 0.037 | 0.027 | 0.025 | 0.023 | 0.031 | 0.027 | 0.028333
24 | 0.028 | 0.029 | 0.026 | 0.024 | 0.022 | 0.025 | 0.025667
25 | 0.03 | 0.026 | 0.028 | 0.033 | 0.034 | 0.034 | 0.030833
26 | 0.039 | 0.042 | 0.029 | 0.026 | 0.024 | 0.026 | 0.031
27 | 0.02 | 0.024 | 0.025 | 0.032 | 0.036 | 0.038 | 0.029167
28 | 0.033 | 0.035 | 0.027 | 0.032 | 0.024 | 0.03 | 0.030167
29 | 0.036 | 0.036 | 0.023 | 0.026 | 0.033 | 0.03 | 0.030667
30 | 0.045 | 0.036 | 0.042 | 0.028 | 0.03 | 0.036 | 0.036167
31
All results are in NTU's
[6 empty] | MIN. | 0.023
[6 empty] | MAX. | 0.041333
[6 empty] | AVG. | 0.030267

## cl2 res
2022-04-01
CHLORINE RESIDUAL
Date | Free | Free | Free | Free | Free | Free
| Chlorine | Chlorine | Chlorine | Chlorine | Chlorine | Chlorine | Average
| Residual | Residual | Residual | Residual | Residual | Residual | Daily
| 12:00 A.M. | 4:00 A.M. | 8:00 A.M. | 12:00 P.M. | 4:00 P.M. | 8:00 P.M. | Residual
1 | 1.27 | 1.25 | 1.24 | 1.24 | 1.3 | 1.36 | 1.2767
2 | 1.28 | 1.29 | 1.33 | 1.28 | 1.33 | 1.27 | 1.2967
3 | 1.33 | 1.29 | 1.31 | 1.32 | 1.34 | 1.33 | 1.32
4 | 1.34 | 1.34 | 1.35 | 1.24 | 1.34 | 1.33 | 1.3233
5 | 1.32 | 1.3 | 1.3 | 1.31 | 1.16 | 1.29 | 1.28
6 | 1.28 | 1.29 | 1.3 | 1.32 | 1.35 | 1.36 | 1.3167
7 | 1.35 | 1.36 | 1.29 | 1.37 | 1.29 | 1.41 | 1.345
8 | 1.29 | 1.23 | 1.34 | 1.33 | 1.39 | 1.22 | 1.3
9 | 1.16 | 1.21 | 1.19 | 1.24 | 1.2 | 1.23 | 1.205
10 | 1.2 | 1.3 | 1.19 | 1.21 | 1.25 | 1.23 | 1.23
11 | 1.25 | 1.23 | 1.24 | 1.24 | 1.24 | 1.25 | 1.2417
12 | 1.24 | 1.23 | 1.12 | 1.22 | 1.16 | 1.2 | 1.195
13 | 1.19 | 1.18 | 1.2 | 1.17 | 1.19 | 1.17 | 1.1833
14 | 1.2 | 1.19 | 1.21 | 1.32 | 1.41 | 1.29 | 1.27
15 | 1.24 | 1.17 | 1.24 | 1.23 | 1.15 | 1.33 | 1.2267
16 | 1.16 | 1.2 | 1.23 | 1.2 | 1.16 | 1.26 | 1.2017
17 | 1.16 | 1.27 | 1.2 | 1.23 | 1.24 | 1.23 | 1.2217
18 | 1.24 | 1.23 | 1.22 | 1.18 | 1.16 | 1.19 | 1.2033
19 | 1.19 | 1.2 | 1.17 | 1.2 | 1.26 | 1.25 | 1.2117
20 | 1.26 | 1.27 | 1.2 | 1.21 | 1.14 | 1.13 | 1.2017
21 | 1.1 | 1.19 | 1.14 | 1.18 | 1.14 | 1.28 | 1.1717
22 | 1.08 | 1.15 | 1.21 | 1.18 | 1.21 | 1.19 | 1.17
23 | 1.15 | 1.2 | 1.15 | 1.24 | 1.2 | 1.22 | 1.1933
24 | 1.22 | 1.26 | 1.2 | 1.16 | 1.16 | 1.19 | 1.1983
25 | 1.24 | 1.22 | 1.21 | 1.17 | 1.15 | 1.18 | 1.195
26 | 1.19 | 1.2 | 1.18 | 1.19 | 1.18 | 1.19 | 1.1883
27 | 1.17 | 1.19 | 1.16 | 1.18 | 1.17 | 1.2 | 1.1783
28 | 1.24 | 1.17 | 1.19 | 1.2 | 1.15 | 1.24 | 1.1983
29 | 1.06 | 1.11 | 1.16 | 1.15 | 1.14 | 1.19 | 1.135
30 | 1.08 | 1.16 | 1.16 | 1.21 | 1.2 | 1.24 | 1.175
31
All results are in mg/l
[6 empty] | MIN. | 1.135
[6 empty] | MAX. | 1.345
[6 empty] | AVG. | 1.2284

## ozone
2022-04-01
Ozone Residual
Date | Ozone | Ozone | Ozone | Ozone | Ozone | Ozone | Average
| Residual | Residual | Residual | Residual | Residual | Residual | Daily
| 12:00 A.M. | 04:00 A.M. | 08:00 A.M. | 12:00 P.M. | 4:00 P.M. | 8:00 P.M. | Residual
1 | 0.62 | 0.65 | 0.56 | 0.58 | 0.58 | 0.59 | 0.59667
2 | 0.44 | 0.61 | 0.56 | 0.57 | 0.6 | 0.6 | 0.56333
3 | 0.65 | 0.63 | 0.62 | 0.65 | 0.63 | 0.6 | 0.63
4 | 0.61 | 0.6 | 0.67 | 0.64 | 0.59 | 0.59 | 0.61667
5 | 0.62 | 0.63 | 0.63 | 0.68 | 0.56 | 0.55 | 0.61167
6 | 0.55 | 0.56 | 0.5 | 0.55 | 0.6 | 0.6 | 0.56
7 | 0.56 | 0.57 | 0.52 | 0.48 | 0.56 | 0.62 | 0.55167
8 | 0.58 | 0.53 | 0.55 | 0.57 | 0.51 | 0.54 | 0.54667
9 | 0.56 | 0.59 | 0.56 | 0.56 | 0.54 | 0.56 | 0.56167
10 | 0.58 | 0.54 | 0.58 | 0.6 | 0.58 | 0.56 | 0.57333
11 | 0.6 | 0.57 | 0.53 | 0.56 | 0.6 | 0.57 | 0.57167
12 | 0.55 | 0.54 | 0.57 | 0.54 | 0.58 | 0.57 | 0.55833
13 | 0.6 | 0.57 | 0.61 | 0.61 | 0.59 | 0.61 | 0.59833
14 | 0.6 | 0.59 | 0.55 | 0.54 | 0.63 | 0.51 | 0.57
15 | 0.46 | 0.54 | 0.55 | 0.54 | 0.58 | 0.6 | 0.545
16 | 0.58 | 0.54 | 0.57 | 0.53 | 0.54 | 0.58 | 0.55667
17 | 0.56 | 0.56 | 0.51 | 0.52 | 0.56 | 0.54 | 0.54167
18 | 0.55 | 0.54 | 0.6 | 0.68 | 0.68 | 0.61 | 0.61
19 | 0.38 | 0.5 | 0.46 | 0.52 | 0.41 | 0.5 | 0.46167
20 | 0.51 | 0.5 | 0.51 | 0.46 | 0.5 | 0.46 | 0.49
21 | 0.53 | 0.54 | 0.63 | 0.57 | 0.48 | 0.41 | 0.52667
22 | 0.42 | 0.46 | 0.53 | 0.54 | 0.48 | 0.54 | 0.495
23 | 0.44 | 0.53 | 0.5 | 0.44 | 0.52 | 0.49 | 0.48667
24 | 0.47 | 0.444 | 0.44 | 0.53 | 0.52 | 0.42 | 0.47067
25 | 0.48 | 0.44 | 0.54 | 0.48 | 0.47 | 0.45 | 0.47667
26 | 0.5 | 0.56 | 0.48 | 0.42 | 0.42 | 0.45 | 0.47167
27 | 0.47 | 0.48 | 0.47 | 0.52 | 0.54 | 0.47 | 0.49167
28 | 0.45 | 0.43 | 0.46 | 0.52 | 0.47 | 0.45 | 0.46333
29 | 0.45 | 0.39 | 0.52 | 0.55 | 0.45 | 0.44 | 0.46667
30 | 0.41 | 0.48 | 0.44 | 0.54 | 0.48 | 0.47 | 0.47
31
All results are in mg/l
[6 empty] | MIN. | 0.46167
[6 empty] | MAX. | 0.63
[6 empty] | AVG. | 0.5378

## Fluoride
2022-04-01
FLUORIDE RESIDUAL
Date | Fluoride | Fluoride | Fluoride | Fluoride | Fluoride | Fluoride | Average
| Residual | Residual | Residual | Residual | Residual | Residual | Daily
| 12:00 A.M. | 04:00 A.M. | 08:00 A.M. | 12:00 P.M. | 4:00 P.M. | 8:00 P.M. | Residual
1 | 0.74 | 0.69 | 0.6 | 0.68 | 0.76 | 0.7 | 0.695
2 | 0.77 | 0.77 | 0.67 | 0.68 | 0.69 | 0.67 | 0.70833
3 | 0.75 | 0.69 | 0.7 | 0.7 | 0.76 | 0.74 | 0.72333
4 | 0.69 | 0.67 | 0.81 | 0.67 | 0.76 | 0.7 | 0.71667
5 | 0.77 | 0.74 | 0.61 | 0.71 | 0.6 | 0.67 | 0.68333
6 | 0.62 | 0.71 | 0.7 | 0.4 | 0.6 | 0.6 | 0.605
7 | 0.62 | 0.64 | 0.75 | 0.78 | 0.76 | 0.8 | 0.725
8 | 0.72 | 0.72 | 0.77 | 0.76 | 0.78 | 0.78 | 0.755
9 | 0.74 | 0.7 | 0.79 | 0.75 | 0.7 | 0.6 | 0.71333
10 | 0.62 | 0.63 | 0.77 | 0.78 | 0.7 | 0.6 | 0.68333
11 | 0.62 | 0.68 | 0.6 | 0.67 | 0.65 | 0.61 | 0.63833
12 | 0.64 | 0.7 | 0.64 | 0.63 | 0.65 | 0.62 | 0.64667
13 | 0.66 | 0.69 | 0.78 | 0.73 | 0.8 | 0.74 | 0.73333
14 | 0.7 | 0.78 | 0.79 | 0.78 | 0.67 | 0.8 | 0.75333
15 | 0.74 | 0.73 | 0.77 | 0.73 | 0.71 | 0.75 | 0.73833
16 | 0.78 | 0.8 | 0.69 | 0.78 | 0.79 | 0.78 | 0.77
17 | 0.76 | 0.79 | 0.8 | 0.84 | 0.77 | 0.6 | 0.76
18 | 0.62 | 0.61 | 0.61 | 0.61 | 0.6 | 0.62 | 0.61167
19 | 0.64 | 0.65 | 0.6 | 0.6 | 0.6 | 0.6 | 0.615
20 | 0.62 | 0.66 | 0.52 | 0.73 | 0.79 | 0.71 | 0.67167
21 | 0.73 | 0.74 | 0.71 | 0.71 | 0.66 | 0.78 | 0.72167
22 | 0.78 | 0.8 | 0.77 | 0.71 | 0.77 | 0.71 | 0.75667
23 | 0.74 | 0.75 | 0.78 | 0.8 | 0.76 | 0.75 | 0.76333
24 | 0.8 | 0.8 | 0.74 | 0.78 | 0.78 | 0.74 | 0.77333
25 | 0.776 | 0.79 | 0.8 | 0.79 | 0.77 | 0.78 | 0.78433
26 | 0.78 | 0.8 | 0.78 | 0.8 | 0.6 | 0.75 | 0.75167
27 | 0.67 | 0.79 | 0.77 | 0.77 | 0.72 | 0.8 | 0.75333
28 | 0.75 | 0.8 | 0.68 | 0.72 | 0.64 | 0.7 | 0.715
29 | 0.69 | 0.69 | 0.73 | 0.67 | 0.7 | 0.71 | 0.69833
30 | 0.78 | 0.78 | 0.66 | 0.65 | 0.65 | 0.8 | 0.72
31
All results are in mg/l
[6 empty] | MIN. | 0.605
[6 empty] | MAX. | 0.78433
[6 empty] | AVG. | 0.71281

## o3srvc
| Service Water |  | 2022-04-22 |  |  | Cooling Water |  |  | service wtr
Date | HIGH | HIGH | LOW | LOW | TOTAL |  |  |  | minus
| Reading 12AM | Flow | Reading 12AM | Flow | FLOW | Reading 12AM |  | Date | cooling wtr
1 | 18748580 | 0 | 6135744 | 0.015401 | 0.015401 | 17544200 | 0.028873 | 1 | -0.013471
2 | 18748580 | 0 | 6137803 | 0.015416 | 0.015416 | 17548060 | 0.029022 | 2 | -0.013606
3 | 18748580 | 0 | 6139864 | 0.015461 | 0.015461 | 17551940 | 0.028948 | 3 | -0.013486
4 | 18748580 | 0.0005236 | 6141931 | 0.015828 | 0.016351 | 17555810 | 0.028499 | 4 | -0.012148
5 | 18748650 | 0 | 6144047 | 0.015356 | 0.015356 | 17559620 | 0.029022 | 5 | -0.013666
6 | 18748650 | 0 | 6146100 | 0.015424 | 0.015424 | 17563500 | 0.029471 | 6 | -0.014047
7 | 18748650 | 0 | 6148162 | 0.012058 | 0.012058 | 17567440 | 0.023637 | 7 | -0.011579
8 | 18748650 | 0.0004488 | 6149774 | 0.015888 | 0.016336 | 17570600 | 0.02992 | 8 | -0.013584
9 | 18748710 | 0 | 6151898 | 0.015214 | 0.015214 | 17574600 | 0.029621 | 9 | -0.014406
10 | 18748710 | 0 | 6153932 | 0.018513 | 0.018513 | 17578560 | 0.035979 | 10 | -0.017466
11 | 18748710 | 0 | 6156407 | 0.015439 | 0.015439 | 17583370 | 0.029995 | 11 | -0.014556
12 | 18748710 | 0 | 6158471 | 0.015349 | 0.015349 | 17587380 | 0.029845 | 12 | -0.014496
13 | 18748710 | 0.0004488 | 6160523 | 0.016067 | 0.016516 | 17591370 | 0.029995 | 14 | -0.013479
14 | 18748770 | 0 | 6162671 | 0.012267 | 0.012267 | 17595380 | 0.023637 | 14 | -0.01137
15 | 18748770 | 0.000374 | 6164311 | 0.015469 | 0.015843 | 17598540 | 0.029396 |  | -0.013554
16 | 18748820 | 0 | 6166379 | 0.015469 | 0.015469 | 17602470 | 0.029995 | 15 | -0.014526
17 | 18748820 | 0.000374 | 6168447 | 0.01867 | 0.019044 | 17606480 | 0.035231 | 16 | -0.016187
18 | 18748870 | 0.0005984 | 6170943 | 0.016015 | 0.016613 | 17611190 | 0.029621 | 17 | -0.013008
19 | 18748950 | 0 | 6173084 | 0.015304 | 0.015304 | 17615150 | 0.029696 | 18 | -0.014392
20 | 18748950 | 0 | 6175130 | 0.012245 | 0.012245 | 17619120 | 0.023637 | 19 | -0.011392
21 | 18748950 | 0 | 6176767 | 0.015446 | 0.015446 | 17622280 | 0.029621 | 20 | -0.014175
22 | 18748950 | 0.0005236 | 6178832 | 0.015514 | 0.016037 | 17626240 | 0.029172 | 21 | -0.013135
23 | 18749020 | 0 | 6180906 | 0.018558 | 0.018558 | 17630140 | 0.036054 | 22 | -0.017496
24 | 18749020 | 0.0004488 | 6183387 | 0.015753 | 0.016202 | 17634960 | 0.029621 | 23 | -0.013419
25 | 18749080 | 0 | 6185493 | 0.015244 | 0.015244 | 17638920 | 0.029471 | 24 | -0.014227
26 | 18749080 | 0 | 6187531 | 0.015379 | 0.015379 | 17642860 | 0.029696 | 25 | -0.014317
27 | 18749080 | 0 | 6189587 | 0.012073 | 0.012073 | 17646830 | 0.023338 | 26 | -0.011265
28 | 18749080 | 0 | 6191201 | 0.015222 | 0.015222 | 17649950 | 0.029322 | 27 | -0.0141
29 | 18749080 | 0 | 6193236 | 0.01496 | 0.01496 | 17653870 | 0.028798 | 28 | -0.013838
30 | 18749080 | 0 | 6195236 | 0.015865 | 0.015865 | 17657720 | 0.030294 | 29 | -0.014429
31 | [7 empty] | 31
1 | 18749080 |  | 6197357 |  |  | 17661770 |  | 1
SUM |  | 0.00374 |  | 0.46087 | 0.46461 |  | 0.87942
AVG |  | 0.00012467 |  | 0.015345 | 0.015469 |  | 0.02928

## NYC flows
| Catskill |  |  | Croton |  | Pump Station
Date | DIGITAL |  |  | 2022-04-01 |  |  | DIGITAL |  |  |  | Average flow | MECHANICAL |  | MECHANICAL
| Reading | Flow |  | Reading 12A | Flow | Flow | Reading | Date | service water | % LOSS |  | Catskill Reading | Flow | Pump Station Reading | Flow | Percent Difference wrt Digital
1 | 28320550 | 2.592 |  |  | 0 | 2.591 | 13073732 | 1 | 0.015401 | 0.63277 | 2.591 | 28124174 | 2.592 | 29136210 | 2.591 | Castsikll Flow | Pump Station Flow | Catskill Reading | Pumpstation Reading
2 | 28323142 | 2.513 |  |  | 0 | 2.535 | 13076323 | 2 | 0.015416 | -0.26199 | 2.535 | 28126766 | 2.513 | 29138801 | 2.535 | 0% | 0% | 0.6933% | -122.8%
3 | 28325655 | 2.488 |  |  | 0 | 2.475 | 13078858 | 3 | 0.015461 | 1.1439 | 2.475 | 28129279 | 2.489 | 29141336 | 2.475 | -0.04019% | 0% | 0.6933% | -122.8%
4 | 28328143 | 2.442 |  |  | 0 | 2.459 | 13081333 | 4 | 0.016351 | -0.026565 | 2.459 | 28131768 | 2.441 | 29143811 | 2.459 | 0.04095% | 0% | 0.6932% | -122.8%
5 | 28330585 | 2.173 |  | 231864 | 0.411 | 2.646 | 13083792 | 5 | 0.015356 | -21.0604 | 2.646 | 28134209 | 2.174 | 29146270 | 2.647 | -0.04602% | -0.03779% | 0.6932% | -122.8%
6 | 28332758 | 2.683 |  | 232275 | 0 | 2.692 | 13086438 | 6 | 0.015424 | 0.23942 | 2.692 | 28136383 | 2.682 | 29148917 | 2.691 | 0.03727% | 0.03715% | 0.6931% | -122.7%
7 | 28335441 | 2.074 |  |  | 0 | 2.041 | 13089130 | 7 | 0.012058 | 2.1725 | 2.041 | 28139065 | 2.074 | 29151608 | 2.041 | 0% | 0% | 0.693% | -122.7%
8 | 28337515 | 2.511 |  |  | 0 | 2.597 | 13091171 | 8 | 0.016336 | -2.7743 | 2.597 | 28141139 | 2.511 | 29153649 | 2.597 | 0% | 0% | 0.693% | -122.7%
9 | 28340026 | 2.52 |  |  | 0 | 2.518 | 13093768 | 9 | 0.015214 | 0.68311 | 2.518 | 28143650 | 2.521 | 29156246 | 2.519 | -0.03968% | -0.03971% | 0.6929% | -122.7%
10 | 28342546 | 2.953 |  |  | 0 | 2.961 | 13096286 | 10 | 0.018513 | 0.35601 | 2.961 | 28146171 | 2.952 | 29158765 | 2.96 | 0.03386% | 0.03377% | 0.6929% | -122.6% | 0
11 | 28345499 | 2.363 |  |  | 0 | 2.405 | 13099247 | 11 | 0.015439 | -1.124 | 2.405 | 28149123 | 2.363 | 29161725 | 2.405 | 0% | 0% | 0.6928% | -122.6%
12 | 28347862 | 2.226 |  |  | 0 | 2.292 | 13101652 | 12 | 0.015349 | -2.2754 | 2.292 | 28151486 | 2.226 | 29164130 | 2.292 | 0% | 0% | 0.6927% | -122.6%
13 | 28350088 | 2.425 |  |  | 0 | 2.435 | 13103944 | 13 | 0.016516 | 0.26869 | 2.435 | 28153712 | 2.425 | 29166422 | 2.435 | 0% | 0% | 0.6927% | -122.6%
14 | 28352513 | 2.105 |  |  | 0 | 2.149 | 13106379 | 14 | 0.012267 | -1.5075 | 2.149 | 28156137 | 2.105 | 29168857 | 2.149 | 0% | 0% | 0.6926% | -122.6%
15 | 28354618 | 2.636 |  |  | 0 | 2.688 | 13108528 | 15 | 0.015843 | -1.3717 | 2.688 | 28158242 | 2.636 | 29171006 | 2.689 | 0% | -0.0372% | 0.6926% | -122.5%
16 | 28357254 | 2.44 |  |  | 0 | 2.442 | 13111216 | 16 | 0.015469 | 0.55199 | 2.442 | 28160878 | 2.44 | 29173695 | 2.441 | 0% | 0.04095% | 0.6925% | -122.5%
17 | 28359694 | 2.961 |  |  | 0 | 3.073 | 13113658 | 17 | 0.019044 | -3.1393 | 3.073 | 28163318 | 2.961 | 29176136 | 3.073 | 0% | 0% | 0.6924% | -122.5%
18 | 28362655 | 2.806 |  |  | 0 | 2.858 | 13116731 | 18 | 0.016613 | -1.2611 | 2.858 | 28166279 | 2.808 | 29179209 | 2.86 | -0.07128% | -0.06998% | 0.6924% | -122.5%
19 | 28365461 | 2.507 |  |  | 0 | 2.53 | 13119589 | 19 | 0.015304 | -0.30698 | 2.53 | 28169087 | 2.507 | 29182069 | 2.53 | 0% | 0% | 0.6923% | -122.4%
20 | 28367968 | 2.029 |  |  | 0 | 2.035 | 13122119 | 20 | 0.012245 | 0.30778 | 2.035 | 28171594 | 2.029 | 29184599 | 2.035 | 0% | 0% | 0.6922% | -122.4%
21 | 28369997 | 2.99 |  |  | 0 | 3.01 | 13124154 | 21 | 0.015446 | -0.1523 | 3.01 | 28173623 | 2.99 | 29186634 | 3.015 | 0% | -0.1661% | 0.6922% | -122.4%
22 | 28372987 | 2.657 |  |  | 0 | 2.704 | 13127164 | 22 | 0.016037 | -1.1653 | 2.704 | 28176613 | 2.669 | 29189649 | 2.709 | -0.4516% | -0.1849% | 0.6921% | -122.4%
23 | 28375644 | 3.226 |  |  | 0 | 3.216 | 13129868 | 23 | 0.018558 | 0.88524 | 3.216 | 28179282 | 3.226 | 29192358 | 3.217 | 0% | -0.03109% | 0.692% | -122.3%
24 | 28378870 | 2.638 |  |  | 0 | 2.645 | 13133084 | 24 | 0.016202 | 0.34881 | 2.645 | 28182508 | 2.638 | 29195575 | 2.645 | 0% | 0% | 0.6919% | -122.3%
25 | 28381508 | 2.89 |  |  | 0 | 2.954 | 13135729 | 25 | 0.015244 | -1.6871 | 2.954 | 28185146 | 2.7 | 29198220 | 2.953 | 6.574% | 0.03385% | 0.6919% | -122.3%
26 | 28384398 | 2.751 |  |  | 0 | 2.781 | 13138683 | 26 | 0.015379 | -0.53148 | 2.781 | 28188036 | 2.75 | 29201173 | 2.781 | 0.03635% | 0% | 0.6918% | -122.3%
27 | 28387149 | 2.353 |  |  | 0 | 2.363 | 13141464 | 27 | 0.012073 | 0.088088 | 2.363 | 28190786 | 2.354 | 29203954 | 2.363 | -0.0425% | 0% | 0.6917% | -122.2%
28 | 28389502 | 2.719 |  |  | 0 | 2.722 | 13143827 | 28 | 0.015222 | 0.4495 | 2.722 | 28193140 | 2.719 | 29206317 | 2.722 | 0% | 0% | 0.6917% | -122.2%
29 | 28392221 | 2.932 |  |  | 0 | 2.954 | 13146549 | 29 | 0.01496 | -0.24011 | 2.954 | 28195859 | 2.932 | 29209039 | 2.953 | 0% | 0.03385% | 0.6916% | -122.2%
30 | 28395153 | 2.913 |  |  |  | 2.929 | 13149503 | 30 | 0.015865 | -0.0046317 | 2.929 | 28198791 | 2.915 | 29211992 |  | -0.06866% | 100% | 0.6915% | -122.2%
31 | [7 empty] | 31 | [9 empty] | #DIV/0! | #DIV/0!
1 | 28398066 | [5 empty] | 13152432 | 1 |  |  |  | 28201706 |  | 29214925 |  |  |  | 0.6915% | -122.1%
SUM |  | 77.516 | 0 |  | 0.411 | 78.7
AVG |  | 2.5839 | #DIV/0! |  | 0.014172 | 2.6233 |  |  |  |  | 78.7 |  | 77.342 |  | 75.782 | -2893% | -2789%
| sum check | 77.516 | 28398.0634 |  | 0.411 | 78.7
| avg check | 2.5839 | 946.6021 |  | 0.0137 | 2.6233
Postive Diffrence Value Means the Digital Is Higher Negative Means the Mechanical is Higher

## LAB
LAB RESULTS
2022-04-22 | [18 empty] | DAILY LABORATORY TESTING
RAW WATER | [7 empty] | PUMP STATION | [10 empty] | Date | DISTRIBUTION SAMPLE
DAY | TEMP. oC | pH | TURB. | COLOR | ALK | HARDNSS | F- | TEMP.oC | pH | TURB. | COLOR | ALK | HARD. | F CL2 | T CL2 | F- | PHOS. | Int. | DAY | TEMP | pH | TURB. | COLOR | ALK | HARD. | F CL2 | T CL2 | F- | PHOS. | initials | Location
1 | 12.9 | 6.96 | 2.44 | 13 | 12 | 14 | 0.04 | 14.9 | 7.56 | 0.024 | 0 | 15 | 16 | 1.27 | 1.29 | 0.74 | 1.59 | MG | 1 | 15.5 | 7.42 | 0.034 | 0 | 14 | 10 | 1.04 | 1.05 | 0.6 | 1.6 | Vin | Town Hall
2 | 10.1 | 7 | 2.52 | 14 | 12 | 14 | 0 | 12.6 | 7.57 | 0.023 | 0 | 14 | 15 | 1.28 | 1.37 | 0.77 | 1.7 | MG | 2 | 14.4 | 7.5 | 0.033 | 0 | 15 | 15 | 1.16 | 1.33 | 0.69 | 1.64 | Vin | Bedford
3 | 10.1 | 7.02 | 2.41 | 13 | 12 | 14 | 0.04 | 12.8 | 7.65 | 0.029 | 0 | 13 | 15 | 1.33 | 1.39 | 0.75 | 1.64 | MG | 3 | 15.9 | 7.87 | 0.045 | 0 | 16 | 16 | 0.93 | 1.01 | 0.79 | 1.63 | Phil | Mt. Peak
4 | 10.3 | 7.1 | 2.51 | 12 | 12 | 12 | 0.02 | 12.9 | 7.61 | 0.025 | 0 | 14 | 15 | 1.34 | 1.39 | 0.69 | 1.6 | MA | 4 | 14.2 | 8.02 | 0.044 | 0 | 12 | 14 | 0.95 | 1.03 | 0.71 | 1.65 | TH | Red Oak
5 | 10.5 | 7.13 | 2.3 | 14 | 12 | 13 | 0 | 12.7 | 7.5 | 0.029 | 0 | 15 | 15 | 1.32 | 1.4 | 0.77 | 1.64 | MA | 5 | 13.8 | 7.45 | 0.036 | 0 | 15 | 16 | 0.94 | 1.04 | 0.71 | 1.44 | phil | campfire rd.
6 | 12.3 | 6.98 | 2.33 | 10 | 11 | 13 | 0.01 | 13.5 | 7.45 | 0.027 | 0 | 22 | 32 | 1.28 | 1.38 | 0.62 | 1.6 | MA | 6 | 16.9 | 8.23 | 0.038 | 0 | 17 | 17 | 0.97 | 1.07 | 0.6 | 1.59 | Phil | DPW
7 | 12.5 | 7.05 | 2.53 | 11 | 12 | 13 | 0 | 14.5 | 7.42 | 0.024 | 0 | 12 | 16 | 1.35 | 1.43 | 0.62 | 1.65 | MA | 7 | 13.1 | 7.32 | 0.039 | 0 | 14 | 14 | 1.26 | 1.34 | 0.8 | 1.67 | MG | Shingle House Road
8 | 13.4 | 7.33 | 2.33 | 13 | 13 | 13 | 0 | 13.2 | 7.46 | 0.035 | 0 | 15 | 15 | 1.29 | 1.3 | 0.72 | 1.6 | vin | 8 | 15.7 | 7.53 | 0.035 | 0 | 14 | 16 | 1.09 | 1.23 | 0.66 | 1.67 | MG | Town Hall
9 | 12.4 | 7.34 | 2.48 | 13 | 14 | 10 | 0 | 12.8 | 7.4 | 0.045 | 0 | 15 | 13 | 1.16 | 1.33 | 0.74 | 1.66 | vin | 9 | 16.9 | 7.35 | 0.033 | 0 | 12 | 14 | 1.01 | 1.13 | 0.76 | 1.68 | MG | Bedford
10 | 13.1 | 7.44 | 2.76 | 14 | 13 | 19 | 0 | 14.2 | 7.5 | 0.037 | 0 | 11 | 14 | 1.2 | 1.35 | 0.62 | 1.36 | vin | 10 | 16.4 | 7.64 | 0.031 | 0 | 14 | 17 | 0.66 | 1.11 | 0.67 | 1.61 | Phil | Mt. Peak
11 | 13.1 | 7.42 | 2.43 | 11 | 14 | 18 | 0 | 13.9 | 7.42 | 0.019 | 0 | 15 | 13 | 1.25 | 1.35 | 0.62 | 1.64 | MA | 11 | 14 | 7.95 | 0.067 | 0 | 14 | 16 | 0.91 | 0.98 | 0.6 | 1.73 | Phil | Red Oak
12 | 13.8 | 7.4 | 2.32 | 12 | 14 | 17 | 0.02 | 13.9 | 7.51 | 0.026 | 0 | 14 | 14 | 1.24 | 1.34 | 0.64 | 1.66 | MA | 12 | 14.2 | 7.61 | 0.026 | 0 | 15 | 16 | 1.01 | 1.12 | 0.6 | 1.64 | Phil | campfire rd.
13 | 13.9 | 7.43 | 2.44 | 11 | 14 | 16 | 0 | 14 | 7.6 | 0.02 | 0 | 14 | 15 | 1.19 | 1.29 | 0.66 | 1.65 | MA | 13 | 16.9 | 7.98 | 0.047 | 0 | 16 | 15 | 0.91 | 0.98 | 0.73 | 1.67 | MG | DPW
14 | 13.8 | 7.4 | 3.32 | 12 | 15 | 15 | 0 | 14.2 | 7.55 | 0.03 | 0 | 14 | 16 | 1.2 | 1.3 | 0.7 | 1.59 | MA | 14 | 15.3 | 7.69 | 0.035 | 0 | 14 | 16 | 1.12 | 1.18 | 0.77 | 1.68 | MG | Shingle House Road
15 | 15.9 | 7.51 | 2.77 | 25 | 13 | 14 | 0 | 16.6 | 7.44 | 0.049 | 0 | 15 | 10 | 1.24 | 1.29 | 0.74 | 1.74 | vin | 15 | 18.2 | 7.57 | 0.092 | 0 | 14 | 15 | 1.06 | 1.14 | 0.7 | 1.66 | MG | Town Hall
16 | 15.6 | 7.5 | 2.21 | 10 | 14 | 14 | 0 | 15.6 | 7.53 | 0.047 | 0 | 15 | 11 | 1.16 | 1.34 | 0.78 | 1.59 | vin | 16 | 18.6 | 7.65 | 0.036 | 0 | 13 | 14 | 1.01 | 1.1 | 0.77 | 1.7 | MG | Bedford
17 | 15.5 | 7.56 | 1.61 | 6 | 15 | 13 | 0 | 13.4 | 7.52 | 0.035 | 0 | 15 | 10 | 1.16 | 1.3 | 0.67 | 1.63 | vin | 17 | 17.9 | 7.91 | 0.091 | 0 | 16 | 16 | 0.83 | 0.91 | 0.8 | 1.8 | Phil | Mt. Peak
18 | 12.7 | 7.49 | 1.89 | 8 | 15 | 14 | 0 | 13.4 | 7.45 | 0.03 | 0 | 14 | 13 | 1.24 | 1.34 | 0.062 | 1.66 | MA | 18 | 17.1 | 7.9 | 0.039 | 0 | 15 | 16 | 0.83 | 0.96 | 0.66 | 1.72 | Phil | Red Oak
19 | 12.9 | 7.41 | 3.53 | 9 | 14 | 14 | 0 | 13.2 | 7.59 | 0.031 | 0 | 14 | 16 | 1.19 | 1.29 | 0.64 | 1.67 | MA | 19 | 15.6 | 7.56 | 0.049 | 0 | 14 | 16 | 0.97 | 1.09 | 0.62 | 1.68 | Phil | campfire rd.
20 | 12.6 | 7.44 | 2.29 | 8 | 13 | 14 | 0.01 | 13.5 | 7.56 | 0.029 | 0 | 14 | 15 | 1.26 | 1.35 | 0.62 | 1.67 | MA | 20 | 16.4 | 8.07 | 0.031 | 0 | 16 | 17 | 0.8 | 0.9 | 0.6 | 1.66 | Phil | DPW
21 | 15.3 | 7.45 | 2.71 | 12 | 16 | 13 | 0 | 17.1 | 7.59 | 0.039 | 0 | 13 | 13 | 1.1 | 1.2 | 0.73 | 1.49 | vin | 20 | 13.7 | 7.35 | 0.043 | 0 | 15 | 14 | 1.18 | 1.19 | 0.7 | 1.65 | MG | Shingle House Road
22 | 17.2 | 7.54 | 1.97 | 12 | 16 | 13 | 0 | 18.6 | 7.7 | 0.025 | 0 | 14 | 12 | 1.08 | 1.23 | 0.78 | 1.7 | vin | 21 | 17.5 | 7.63 | 0.029 | 0 | 14 | 14 | 1.01 | 1.04 | 0.76 | 1.7 | MG | Town Hall
23 | 18.7 | 7.59 | 1.94 | 12 | 12 | 11 | 0 | 15.4 | 7.36 | 0.037 | 0 | 12 | 10 | 1.15 | 1.21 | 0.74 | 1.54 | vin | 23 | 18.1 | 7.51 | 0.043 | 0 | 14 | 15 | 0.92 | 1.01 | 0.79 | 1.73 | MG | Bedford
24 | 13.6 | 7.24 | 1.65 | 9 | 10 | 14 | 0.17 | 17.3 | 7.31 | 0.028 | 0 | 12 | 14 | 1.22 | 1.32 | 0.8 | 1.62 | TH | 24 | 16.9 | 7.73 | 0.078 | 0 | 14 | 17 | 0.72 | 0.85 | 0.79 | 1.8 | Phil | Mt. Peak
25 | 12.9 | 7.32 | 1.7 | 9 | 11 | 14 | 0.03 | 16.9 | 7.48 | 0.03 | 0 | 12 | 14 | 1.24 | 1.33 | 0.73 | 1.65 | MA | 25 | 16.9 | 7.75 | 0.026 | 0 | 17 | 18 | 0.81 | 0.89 | 0.79 | 1.66 | Phil | Red Oak
26 | 12.8 | 7.4 | 1.39 | 8 | 10 | 13 | 0.01 | 16.7 | 7.53 | 0.029 | 0 | 14 | 14 | 1.19 | 1.29 | 0.78 | 1.66 | MA | 26 | 15.1 | 7.52 | 0.04 | 0 | 15 | 16 | 0.94 | 1 | 0.6 | 1.71 | Phil | campfire rd.
27 | 12.9 | 7.37 | 1.39 | 9 | 11 | 14 | 0 | 16.8 | 7.49 | 0.024 | 0 | 15 | 16 | 1.17 | 1.27 | 0.67 | 1.64 | MA | 27 | 17.5 | 8.04 | 0.052 | 0 | 14 | 16 | 0.73 | 0.82 | 0.76 | 1.77 | MG | DPW
28 | 15.6 | 7.46 | 1.53 | 14 | 13 | 11 | 0 | 15.9 | 7.45 | 0.033 | 0 | 11 | 12 | 1.24 | 1.31 | 0.75 | 1.14 | vin | 28 | 17.5 | 7.48 | 0.049 | 0 | 12 | 14 | 1.07 | 1.17 | 0.79 | 1.88 | MG | Shingle House Road
29 | 18.2 | 7.58 | 1.83 | 13 | 13 | 12 | 0.02 | 18.2 | 7.72 | 0.036 | 0 | 12 | 12 | 1.06 | 1.18 | 0.69 | 1.68 | vin | 29 | 16.1 | 7.48 | 0.029 | 0 | 13 | 14 | 0.9 | 1.01 | 0.67 | 2.02 | MG | Town Hall
30 | 16.8 | 7.77 | 2.02 | 11 | 14 | 13 | 0 | 17.8 | 7.71 | 0.045 | 0 | 17 | 13 | 1.08 | 1.21 | 0.78 | 1.54 | vin | 30 | 16.5 | 7.74 | 0.031 | 0 | 16 | 14 | 0.98 | 1.09 | 0.77 | 1.64 | MG | Bedford
31

## daf
DAF TURBIDTY | [11 empty] | COMBINE RAW TURB. | % REMOVAL | 2021 DAF TURBIDITY TESTING | [10 empty] | COMBINE RAW TURB. | % REMOVAL
DATE | TIME | #1 | #2 | #3 | #4 | #5 | FLOW | GPM | PSI | COMPUTR | BENCH |  |  | DATE | #1 | #2 | #3 | #4 | #5 | FLOW | GPM | PSI | COMPUTR | BENCH
1 | 1235am | x | x | x | x | x | 2.84 | 422 | 48 | 0.17 | 0.088 | 2.44 | 96.3934 | 1 | 0.12 | 0.107 | 0.137 | 0.109 | #DIV/0! | 2.85 | 423 | 47.5 | 0.19 | 0.1045 | 2.46 | 95.752
1 | 2pm | 0.12 | 0.107 | 0.137 | 0.109 | x | 2.86 | 424 | 47 | 0.21 | 0.121 | 2.48 | 95.121 | 2 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2.925 | 422.5 | 47.5 | 0.12 | 0.084 | 2.5 | 96.64
1 | [12 empty] | 95.121 | 3 | 0.149 | 0.129 | 0.139 | 0.174 | #DIV/0! | 2.68 | 422.5 | 47.5 | 0.14 | 0.0915 | 2.43 | 96.2346
|  | 0.12 | 0.107 | 0.137 | 0.109 | #DIV/0! | 2.85 | 423 | 47.5 | 0.19 | 0.1045 | 2.46 | 95.752 | 4 | 0.136 | 0.124 | 0.146 | 0.166 | #DIV/0! | 2.81 | 424.5 | 47 | 0.15 | 0.104 | 2.33 | 95.5365
2 | 1230am | x | x | x | x | x | 2.99 | 423 | 48 | 0.13 | 0.075 | 2.52 | 97.0238 | 5 | 0.182 | 0.13 | 0.135 | 0.157 | #DIV/0! | 2.93 | 224 | 47 | 0.13 | 0.1095 | 2.325 | 95.2903
2 | 2pm | x | x | x | x | x | 2.86 | 422 | 47 | 0.11 | 0.093 | 2.48 | 96.25 | 6 | 0.187 | 0.179 | 0.195 | 0.23 | #DIV/0! | 2.92 | 408.5 | 51.5 | 0.205 | 0.1385 | 2.37 | 94.1561
2 | [12 empty] | #DIV/0! | 7 | 0.168 | 0.156 | 0.17 | 0.19 | #DIV/0! | 3.05 | 420.5 | 48 | 1.29 | 0.1785 | 1.336 | 86.6392
|  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2.925 | 422.5 | 47.5 | 0.12 | 0.084 | 2.5 | 96.64 | 8 | 0.17 | 0.15 | 0.2 | 0.214 | #DIV/0! | 2.88 | 422.5 | 47 | 2.505 | 0.16 | 0.1305 | -22.6054
3 | 12:45am | x | x | x | x | x | 2.75 | 421 | 48 | 0.17 | 0.068 | 2.41 | 97.1784 | 9 | 0.17 | 0.16 | 0.18 | 0.21 | #DIV/0! | 2.64 | 424.5 | 47 | 3.06 | 0.17 | 0.165 | -3.0303
3 | 10:15am | 0.149 | 0.129 | 0.139 | 0.174 | x | 2.61 | 424 | 47 | 0.11 | 0.115 | 2.45 | 95.3061 | 10 | 0.185 | 0.149 | 0.148 | 0.19 | #DIV/0! | 2.715 | 425.5 | 44.5 | 0.13 | 0.1415 | 2.6 | 94.5577
3 | [12 empty] | #DIV/0! | 11 | 0.167 | 0.128 | 0.148 | 0.179 | #DIV/0! | 2.69 | 422 | 47 | 0.11 | 0.0785 | 2.345 | 96.6525
|  | 0.149 | 0.129 | 0.139 | 0.174 | #DIV/0! | 2.68 | 422.5 | 47.5 | 0.14 | 0.0915 | 2.43 | 96.2346 | 12 | 0.154 | 0.127 | 0.183 | 0.192 | #DIV/0! | 2.63 | 422.5 | 30.5 | 0.155 | 0.0895 | 2.455 | 96.3544
3.6471 | 12:20am | x | x | x | x | x | 2.84 | 423 | 47 | 0.12 | 0.08 | 2.51 | 96.8127 | 13 | 0.175 | 0.146 | 0.167 | 0.205 | #DIV/0! | 2.805 | 422 | 47 | 0.125 | 0.078 | 3.085 | 97.4716
3.8824 | 11:35am | 0.136 | 0.124 | 0.146 | 0.166 | x | 2.78 | 426 | 47 | 0.18 | 0.128 | 2.15 | 94.0465 | 14 | 0.16 | 0.15 | 0.16 | 0.19 | #DIV/0! | 2.97 | 422.5 | 45.5 | 0.14 | 0.085 | 3.305 | 97.4281
4.1176 | [12 empty] | #DIV/0! | 15 | 0.14 | 0.12 | 0.13 | 0.143 | #DIV/0! | 3.135 | 422.5 | 47 | 0.14 | 0.099 | 2.89 | 96.5744
|  | 0.136 | 0.124 | 0.146 | 0.166 | #DIV/0! | 2.81 | 424.5 | 47 | 0.15 | 0.104 | 2.33 | 95.5365 | 16 | 0.1 | 0.09 | 0.1 | 0.1 | #DIV/0! | 2.63 | 420.5 | 47.5 | 0.1 | 0.0925 | 2.065 | 95.5206
4.5882 | 12:20am | x | x | x | x | x | 2.77 | 23 | 47 | 0.15 | 0.086 | 2.3 | 96.2609 | 17 | 0.123 | 0.092 | 0.133 | 0.116 | #DIV/0! | 2.83 | 424.5 | 47.5 | 0.09 | 0.0845 | 1.805 | 95.3186
4.8235 | 3:15pm | 0.182 | 0.13 | 0.135 | 0.157 | x | 3.09 | 425 | 47 | 0.11 | 0.133 | 2.35 | 94.3404 | 18 | 0.12 | 0.095 | 0.114 | 0.143 | #DIV/0! | 2.85 | 423.5 | 47.5 | 0.06 | 0.086 | 2.265 | 96.2031
5.0588 | [12 empty] | #DIV/0! | 19 | 0.128 | 0.094 | 0.103 | 0.113 | #DIV/0! | 2.89 | 423 | 47 | 0.055 | 0.148 | 3.325 | 95.5489
|  | 0.182 | 0.13 | 0.135 | 0.157 | #DIV/0! | 2.93 | 224 | 47 | 0.13 | 0.1095 | 2.325 | 95.2903 | 20 | 0.198 | 0.121 | 0.15 | 0.167 | #DIV/0! | 2.635 | 418.5 | 48 | 0.08 | 0.1595 | 2.86 | 94.4231
5.5294 | 12:20am | x | x | x | x | x | 2.93 | 424 | 47 | 0.17 | 0.118 | 2.33 | 94.9356 | 21 | 0.127 | 0.088 | 0.112 | 0.114 | #DIV/0! | 3.255 | 418.5 | 49 | 0.075 | 0.131 | 2.41 | 94.5643
5.7647 | 10:40am | 0.187 | 0.179 | 0.195 | 0.23 | x | 2.91 | 393 | 56 | 0.24 | 0.159 | 2.41 | 93.4025 | 22 | 0.1 | 0.08 | 0.09 | 0.11 | #DIV/0! | 3.085 | 417 | 48 | 0.04 | 0.0675 | 1.65 | 94.961
6 | [12 empty] | #DIV/0! | 23 | 0.095 | 0.089 | 0.09 | 0.109 | #DIV/0! | 2.985 | 417.5 | 48.5 | 0.025 | 0.087 | 1.795 | 95.1532
|  | 0.187 | 0.179 | 0.195 | 0.23 | #DIV/0! | 2.92 | 408.5 | 51.5 | 0.205 | 0.1385 | 2.37 | 94.1561 | 24 | 0.102 | 0.085 | 0.081 | 0.113 | #DIV/0! | 2.95 | 364.5 | 52 | 0.045 | 0.074 | 1.59 | 95.3459
6.7059 | 12:20am | x | x | x | x | x | 3.1 | 423 | 47 | 0.24 | 0.187 | 2.53 | 92.6087 | 25 | 0.088 | 0.088 | 0.077 | 0.098 | #DIV/0! | 2.965 | 417.5 | 49 | 0.075 | 0.08 | 1.565 | 94.8882
6.9412 | 130PM | 0.168 | 0.156 | 0.17 | 0.19 | x | 3 | 418 | 49 | 2.34 | 0.17 | 0.142 | -19.7183 | 26 | 0.091 | 0.082 | 0.087 | 0.085 | #DIV/0! | 3.18 | 416 | 48.5 | 0.05 | 0.073 | 1.38 | 94.7101
7.1765 | [12 empty] | #DIV/0! | 27 | 0.1 | 0.1 | 0.1 | 0.1 | #DIV/0! | 3.2 | 384 | 53 | 0.055 | 0.0815 | 1.53 | 94.6732
|  | 0.168 | 0.156 | 0.17 | 0.19 | #DIV/0! | 3.05 | 420.5 | 48 | 1.29 | 0.1785 | 1.336 | 86.6392 | 28 | 0.1 | 0.09 | 0.09 | 0.11 | #DIV/0! | 3.085 | 417 | 48 | 0.04 | 0.0675 | 1.65 | 95.9091
7.6471 | 12am | x | x | x | x | x | 2.75 | 422 | 47 | 2.33 | 0.14 | 0.142 | 1.4085 | 29 | 0.1 | 0.09 | 0.12 | 0.13 | #DIV/0! | 3.105 | 418 | 48 | 0.03 | 0.094 | 1.865 | 94.9598
7.8824 | 11am | 0.17 | 0.15 | 0.2 | 0.214 | x | 3.01 | 423 | 47 | 2.68 | 0.18 | 0.119 | -51.2605 | 30 | 0.11 | 0.1 | 0.11 | 0.14 | #DIV/0! | 3.1 | 416.5 | 48.5 | 0.045 | 0.076 | 1.925 | 96.0519
8.1176 | [12 empty] | #DIV/0! | 31 | [11 empty] | #DIV/0!
|  | 0.17 | 0.15 | 0.2 | 0.214 | #DIV/0! | 2.88 | 422.5 | 47 | 2.505 | 0.16 | 0.1305 | -22.6054 | DO NOT PUT NUMBERS IN THIS SPREADSHEET IT CONTAINS FORMULA THAT WILL AVERAGE THE DAF TURBIDITY.
8.5882 | 12am | x | x | x | x | x | 2.52 | 425 | 47 | 2.48 | 0.19 | 0.2 | 5
8.8235 | 840am | 0.17 | 0.16 | 0.18 | 0.21 | x | 2.76 | 424 | 47 | 3.64 | 0.15 | 0.13 | -15.3846
9.0588 | [12 empty] | #DIV/0!
|  | 0.17 | 0.16 | 0.18 | 0.21 | #DIV/0! | 2.64 | 424.5 | 47 | 3.06 | 0.17 | 0.165 | -3.0303
9.5294 | 12am | x | x | x | x | x | 2.69 | 427 | 42 | 0.15 | 0.163 | 2.6 | 93.7308
9.7647 | 11:30am | 0.185 | 0.149 | 0.148 | 0.19 | x | 2.74 | 424 | 47 | 0.11 | 0.12 | 2.6 | 95.3846
10 | [12 empty] | #DIV/0!
|  | 0.185 | 0.149 | 0.148 | 0.19 | #DIV/0! | 2.715 | 425.5 | 44.5 | 0.13 | 0.1415 | 2.6 | 94.5577
10.7059 | 12:21am | x | x | x | x | x | 2.65 | 422 | 47 | 0.1 | 0.092 | 2.43 | 96.214
10.9412 | 9:15am | 0.167 | 0.128 | 0.148 | 0.179 | x | 2.73 | 422 | 47 | 0.12 | 0.065 | 2.26 | 97.1239
11.1765 | [12 empty] | #DIV/0!
|  | 0.167 | 0.128 | 0.148 | 0.179 | #DIV/0! | 2.69 | 422 | 47 | 0.11 | 0.0785 | 2.345 | 96.6525
11.6471 | 12:20am | x | x | x | x | x | 2.59 | 422 | 47 | 0.1 | 0.07 | 2.32 | 96.9828
11.8824 | 10:45am | 0.154 | 0.127 | 0.183 | 0.192 | x | 2.67 | 423 | 14 | 0.21 | 0.109 | 2.59 | 95.7915
12.1176 | [12 empty] | #DIV/0!
|  | 0.154 | 0.127 | 0.183 | 0.192 | #DIV/0! | 2.63 | 422.5 | 30.5 | 0.155 | 0.0895 | 2.455 | 96.3544
12.5882 | 12:20am | x | x | x | x | x | 2.82 | 423 | 47 | 0.1 | 0.087 | 2.44 | 96.4344
12.8235 | 1:45pm | 0.175 | 0.146 | 0.167 | 0.205 | x | 2.79 | 421 | 47 | 0.15 | 0.069 | 3.73 | 98.1501
13.0588 | [12 empty] | #DIV/0!
|  | 0.175 | 0.146 | 0.167 | 0.205 | #DIV/0! | 2.805 | 422 | 47 | 0.125 | 0.078 | 3.085 | 97.4716
13.5294 | 12:20am | x | x | x | x | x | 2.81 | 423 | 47 | 0.15 | 0.06 | 3.32 | 98.1928
13.7647 | 210PM | 0.16 | 0.15 | 0.16 | 0.19 | x | 3.13 | 422 | 44 | 0.13 | 0.11 | 3.29 | 96.6565
14 | [12 empty] | #DIV/0!
|  | 0.16 | 0.15 | 0.16 | 0.19 | #DIV/0! | 2.97 | 422.5 | 45.5 | 0.14 | 0.085 | 3.305 | 97.4281
14.7059 | 12am | x | x | x | x | x | 3.36 | 422 | 47 | 0.1 | 0.106 | 2.77 | 96.1733
14.9412 | 10am | 0.14 | 0.12 | 0.13 | 0.143 | x | 2.91 | 423 | 47 | 0.18 | 0.092 | 3.01 | 96.9435
15.1765 | [12 empty] | #DIV/0!
|  | 0.14 | 0.12 | 0.13 | 0.143 | #DIV/0! | 3.135 | 422.5 | 47 | 0.14 | 0.099 | 2.89 | 96.5744
15.6471 | 12am | x | x | x | x | x | 2.8 | 421 | 48 | 0.14 | 0.111 | 2.21 | 94.9774
15.8824 | 830am | 0.1 | 0.09 | 0.1 | 0.1 | x | 2.46 | 420 | 47 | 0.06 | 0.074 | 1.92 | 96.1458
16.1176 | [12 empty] | #DIV/0!
|  | 0.1 | 0.09 | 0.1 | 0.1 | #DIV/0! | 2.63 | 420.5 | 47.5 | 0.1 | 0.0925 | 2.065 | 95.5206
16.5882 | 12am | x | x | x | x | x | 2.55 | 424 | 48 | 0.05 | 0.08 | 1.92 | 95.8333
16.8235 | 8:30am | 0.123 | 0.092 | 0.133 | 0.116 | x | 3.11 | 425 | 47 | 0.13 | 0.089 | 1.69 | 94.7337
17.0588 | [12 empty] | #DIV/0!
|  | 0.123 | 0.092 | 0.133 | 0.116 | #DIV/0! | 2.83 | 424.5 | 47.5 | 0.09 | 0.0845 | 1.805 | 95.3186
17.5294 | 12:20am | x | x | x | x | x | 2.67 | 424 | 47 | 0.05 | 0.079 | 1.89 | 95.8201
17.7647 | 8:30am | 0.12 | 0.095 | 0.114 | 0.143 | x | 3.03 | 423 | 48 | 0.07 | 0.093 | 2.64 | 96.4773
18 | [12 empty] | #DIV/0!
|  | 0.12 | 0.095 | 0.114 | 0.143 | #DIV/0! | 2.85 | 423.5 | 47.5 | 0.06 | 0.086 | 2.265 | 96.2031
18.7059 | 12:19am | x | x | x | x | x | 3.13 | 423 | 47 | 0.05 | 0.15 | 3.53 | 95.7507
18.9412 | 11:15am | 0.128 | 0.094 | 0.103 | 0.113 | x | 2.65 | 423 | 47 | 0.06 | 0.146 | 3.12 | 95.3205
19.1765 | [12 empty] | #DIV/0!
|  | 0.128 | 0.094 | 0.103 | 0.113 | #DIV/0! | 2.89 | 423 | 47 | 0.055 | 0.148 | 3.325 | 95.5489
19.6471 | 12:20am | x | x | x | x | x | 2.77 | 418 | 48 | 0.07 | 0.12 | 2.29 | 94.7598
20.1176 | 9am | 0.198 | 0.121 | 0.15 | 0.167 | x | 2.5 | 419 | 48 | 0.09 | 0.199 | 3.43 | 94.1983
20.3529 | [12 empty] | #DIV/0!
|  | 0.198 | 0.121 | 0.15 | 0.167 | #DIV/0! | 2.635 | 418.5 | 48 | 0.08 | 0.1595 | 2.86 | 94.4231
20.8235 | 12:20am | x | x | x | x | x | 3.15 | 417 | 49 | 0.08 | 0.146 | 2.71 | 94.6125
21.0588 | 9:30am | 0.127 | 0.088 | 0.112 | 0.114 | x | 3.36 | 420 | 49 | 0.07 | 0.116 | 2.11 | 94.5024
21.2941 | [12 empty] | #DIV/0!
|  | 0.127 | 0.088 | 0.112 | 0.114 | #DIV/0! | 3.255 | 418.5 | 49 | 0.075 | 0.131 | 2.41 | 94.5643
21.7647 | 12am | x | x | x | x | x | 2.29 | 415 | 49 | 0.06 | 0.121 | 1.95 | 93.7949
22 | 1045am | 0.1 | 0.08 | 0.11 | 0.11 | x | 3.42 | 416 | 49 | 0.04 | 0.073 | 1.9 | 96.1579
22.2353 | [12 empty] | #DIV/0!
|  | 0.1 | 0.08 | 0.11 | 0.11 | #DIV/0! | 2.855 | 415.5 | 49 | 0.05 | 0.097 | 1.925 | 94.961
23 | 12am | x | x | x | x | x | 3.26 | 420 | 48 | 0.03 | 0.098 | 1.94 | 94.9485
22.9412 | 8:45am | 0.095 | 0.089 | 0.09 | 0.109 | x | 2.71 | 415 | 49 | 0.02 | 0.076 | 1.65 | 95.3939
23.4118 | [12 empty] | #DIV/0!
|  | 0.095 | 0.089 | 0.09 | 0.109 | #DIV/0! | 2.985 | 417.5 | 48.5 | 0.025 | 0.087 | 1.795 | 95.1532
23.8824 | 12am | x | x | x | x | x | 3.16 | 309 | 56 | 0.03 | 0.06 | 1.65 | 96.3636
24.1176 | 10:30am | 0.102 | 0.085 | 0.081 | 0.113 | x | 2.74 | 420 | 48 | 0.06 | 0.088 | 1.53 | 94.2484
24.3529 | [12 empty] | #DIV/0!
|  | 0.102 | 0.085 | 0.081 | 0.113 | #DIV/0! | 2.95 | 364.5 | 52 | 0.045 | 0.074 | 1.59 | 95.3459
25.0588 | 12:20am | x | x | x | x | x | 2.97 | 418 | 49 | 0.06 | 0.079 | 1.7 | 95.3529
25.2941 | 10:45am | 0.088 | 0.088 | 0.077 | 0.098 | x | 2.96 | 417 | 49 | 0.09 | 0.081 | 1.43 | 94.3357
25 | [12 empty] | #DIV/0!
|  | 0.088 | 0.088 | 0.077 | 0.098 | #DIV/0! | 2.965 | 417.5 | 49 | 0.075 | 0.08 | 1.565 | 94.8882
26 | 12:20am | x | x | x | x | x | 3.04 | 415 | 49 | 0.05 | 0.08 | 1.39 | 94.2446
26.2353 | 9:45am | 0.091 | 0.082 | 0.087 | 0.085 | x | 3.32 | 417 | 48 | 0.05 | 0.066 | 1.37 | 95.1825
26 | [12 empty] | #DIV/0!
|  | 0.091 | 0.082 | 0.087 | 0.085 | #DIV/0! | 3.18 | 416 | 48.5 | 0.05 | 0.073 | 1.38 | 94.7101
26.9412 | 12:20am | x | x | x | x | x | 3.21 | 349 | 58 | 0.06 | 0.079 | 1.39 | 94.3165
27.1765 | 1120am | 0.1 | 0.1 | 0.1 | 0.1 | x | 3.19 | 419 | 48 | 0.05 | 0.084 | 1.67 | 94.9701
27.4118 | [12 empty] | #DIV/0!
|  | 0.1 | 0.1 | 0.1 | 0.1 | #DIV/0! | 3.2 | 384 | 53 | 0.055 | 0.0815 | 1.53 | 94.6732
27.8824 | 12am | x | x | x | x | x | 3.19 | 417 | 48 | 0.05 | 0.063 | 1.53 | 95.8824
28 | 945am | 0.1 | 0.09 | 0.09 | 0.11 | x | 2.98 | 417 | 48 | 0.03 | 0.072 | 1.77 | 95.9322
28.3529 | [12 empty] | #DIV/0!
|  | 0.1 | 0.09 | 0.09 | 0.11 | #DIV/0! | 3.085 | 417 | 48 | 0.04 | 0.0675 | 1.65 | 95.9091
28.8235 | 12am | x | x | x | x | x | 2.99 | 419 | 48 | 0.03 | 0.117 | 1.83 | 93.6066
29.0588 | 1245pm | 0.1 | 0.09 | 0.12 | 0.13 | x | 3.22 | 417 | 48 | 0.03 | 0.071 | 1.9 | 96.2632
29.2941 | [12 empty] | #DIV/0!
|  | 0.1 | 0.09 | 0.12 | 0.13 | #DIV/0! | 3.105 | 418 | 48 | 0.03 | 0.094 | 1.865 | 94.9598
30 | 12am | x | x | x | x | x | 2.87 | 415 | 49 | 0.03 | 0.09 | 2.02 | 95.5446
30 | 830am | 0.11 | 0.1 | 0.11 | 0.14 | x | 3.33 | 418 | 48 | 0.06 | 0.062 | 1.83 | 96.612
30.2353 | [12 empty] | #DIV/0!
|  | 0.11 | 0.1 | 0.11 | 0.14 | #DIV/0! | 3.1 | 416.5 | 48.5 | 0.045 | 0.076 | 1.925 | 96.0519
30.7059 | [12 empty] | #DIV/0!
30.9412 | [12 empty] | #DIV/0!
31.1765 | [12 empty] | #DIV/0!
#DIV/0!

## KMNO4
| KMNO4 | KMNO4 | KMNO4 | KMNO4 | KMNO4 | KMNO4 |  | Average
Day | Residual | Residual | Residual | Residual | Residual | Residual |  | Daily
| 12:00 A.M. | 04:00 A.M. | 08:00 A.M. | 12:00 P.M. | 4:00 P.M. | 8:00 P.M. |  | Residual
[8 empty] | RM#2 | DAF | EFF
1 | [7 empty] | 0 | 0 | 0
2 | [7 empty] | 0 | 0 | 0
3 | [7 empty] | 0 | 0 | 0
4 | [7 empty] | 0 | 0 | 0
5 | [7 empty] | 0 | 0 | 0
6 | [7 empty] | 0 | 0 | 0
7 | [7 empty] | 0 | 0 | 0
8 | [7 empty] | 0 | 0 | 0
9 | [7 empty] | 0 | 0 | 0
10 | [7 empty] | 0 | 0 | 0
11 | [7 empty] | 0 | 0 | 0
12 | [7 empty] | 0 | 0 | 0
13 | [7 empty] | 0 | 0 | 0
14 | [7 empty] | 0 | 0 | 0
15 | [7 empty] | 0 | 0 | 0
16 | [7 empty] | 0 | 0 | 0
17 | [7 empty] | 0 | 0 | 0
18 | [7 empty] | 0 | 0 | 0
19 | [7 empty] | 0 | 0 | 0
20 | [7 empty] | 0 | 0 | 0
21 | [7 empty] | 0 | 0 | 0
22 | [7 empty] | 0 | 0 | 0
23 | [7 empty] | 0 | 0 | 0
24 | [7 empty] | 0 | 0 | 0
25 | [7 empty] | 0 | 0 | 0
26 | [7 empty] | 0 | 0 | 0
27 | [7 empty] | 0 | 0 | 0
28 | [7 empty] | 0 | 0 | 0
29 | [7 empty] | 0 | 0 | 0
30 | [7 empty] | 0 | 0 | 0
31 | [7 empty] | 0 | 0 | 0
[7 empty] | MIN. | 0 | 0 | 0
All results are in mg/l | [6 empty] | MAX. | 0 | 0 | 0
[7 empty] | AVG. | 0 | 0 | 0

## THCKNER
Thickener Testing | Time | Raw | washwater | supernate | % | w.w.w. tk
|  | NTU | NTU | NTU | removal | level
AVERAGE |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## REP PG1
Public Water System Name: |  |  |  | Reporting Month/Year |  | Date Report Submitted: |  | Source Type(s)
New Castle Consolidated WD |  |  |  | 2022-04-01 |  |  |  | Surface Water [ x ]
|  |  |  | Town, Village or City |  | M M D D Y Y Y Y |  | Groundwater [ ]
Public Water Supply ID |  |  |  | Millwood |  | County |  | GWUDI [ ]
NY 5903442 |  |  |  |  | Valid waiver from disinfection? Yes [ ] No [ X ] | Westchester
Is filtration provided for surface supply? Yes [ x ] No [ ]
Did an emergency occur in any part of the water system? Yes [ ] No [ x ] |  |  |  |  | Wavier #_________________on Date:______________________
Does system have approval to flouridate? Yes [ x ] No [ ]
Millwood Water Treatment Plant
| TREATED | CHLORINATION |  | LIQUID |  |  | CHEMICALS/OTHER TREATMENT
| WATER | GASEOUS |  | HYPO- |  | FREE |  | Finished
Date | VOLUME | CYLINDER | CHLORINE | CHLORITE |  | CHLORINE | Ortho- | Water | See Others
| (1,000 GALs/ | WEIGHT | USE | Gallons |  | RESIDUAL | Phosphate | Fluoride
| DAY) |  | (LBS/DAY) |  |  | (mg/l) | Gallons | (mg/l) | DOH-1015
1 | 2591 |  | 28.82 |  |  | 1.2767 | 7 | 0.695
2 | 2535 |  | 28.3 |  |  | 1.2967 | 8 | 0.70833
3 | 2475 |  | 27.31 |  |  | 1.32 | 7.5 | 0.72333
4 | 2459 |  | 27.48 |  |  | 1.3233 | 8 | 0.71667
5 | 2646 |  | 29.44 |  |  | 1.28 | 8 | 0.68333
6 | 2692 |  | 29.87 |  |  | 1.3167 | 8 | 0.605
7 | 2041 |  | 29 |  |  | 1.345 | 8 | 0.725
8 | 2597 |  | 30.96 |  |  | 1.3 | 8 | 0.755
9 | 2518 |  | 31.76 |  |  | 1.205 | 8 | 0.71333
10 | 2961 |  | 28.24 |  |  | 1.23 | 7.5 | 0.68333
11 | 2405 |  | 28.01 |  |  | 1.2417 | 7.5 | 0.63833
12 | 2292 |  | 24.73 |  |  | 1.195 | 7 | 0.64667
13 | 2435 |  | 28.09 |  |  | 1.1833 | 8 | 0.73333
14 | 2149 |  | 30 |  |  | 1.27 | 9 | 0.75333
15 | 2688 |  | 26 |  |  | 1.2267 | 8 | 0.73833
16 | 2442 |  | 24.19 |  |  | 1.2017 | 8 | 0.77
17 | 3073 |  | 25.83 |  |  | 1.2217 | 8 | 0.76
18 | 2858 |  | 28.43 |  |  | 1.2033 | 9 | 0.61167
19 | 2530 |  | 24.9 |  |  | 1.2117 | 7.5 | 0.615
20 | 2035 |  | 26.05 |  |  | 1.2017 | 9 | 0.67167
21 | 3010 |  | 29.45 |  |  | 1.1717 | 8 | 0.72167
22 | 2704 |  | 28.51 |  |  | 1.17 | 9 | 0.75667
23 | 3216 |  | 25.73 |  |  | 1.1933 | 9 | 0.76333
24 | 2645 |  | 26.09 |  |  | 1.1983 | 8 | 0.77333
25 | 2954 |  | 29.35 |  |  | 1.195 | 8 | 0.78433
26 | 2781 |  | 27.55 |  |  | 1.1883 | 9 | 0.75167
27 | 2363 |  | 29.6 |  |  | 1.1783 | 9 | 0.75333
28 | 2722 |  | 28.28 |  |  | 1.1983 | 9.5 | 0.715
29 | 2954 |  | 35.6 |  |  | 1.135 | 9.5 | 0.69833
30 | 2929 |  | 32.3 |  |  | 1.175 | 7 | 0.72
31
TOTAL |  |  | 849.87 |  |  | 36.8533 | 245 | 21.3843
AVERAGE | 2623.3333 |  | 28.329 |  |  | 1.2284 | 8.1667 | 0.71281
Reported by: John Young Title: Chief Operator | [6 empty] | Certification Number: NY 0032778
Signature: Grade Level: 1A | [6 empty] | Date: / /

## REP PG2
Sample | Date of | Sample Type | Total Coliform | E.coli | Free | Raw
Location | Sample | 1. Routine | Positive | Positive | Chlorine | Turbidity
|  | 2. Repeat |  |  | Residual
|  | 3. Hi Turb |  |  | mg/l | NTU
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [ ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [ ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [ ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [ ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [ ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [ ] No
Sample Collector: _____________________________ Date: _ / / and / / _____________________
Name of Laboratory:Westchester County City:Valhalla Laboratory ELAP Certification #10108
Population Served 16,900 Number of Routine Samples**15 Number of Actual Routine Samples 15
Does and M&AR Violation Exist? [ ] Yes [ X ] No
If YES, check reason(s) below:
___ Two or more positive total coliform samples for systems collecting less than forty (40) or more samples (routine, repeat, or HiTurb) per month.
___ More than 5% positive total coliform samples for system collecting forty (40) or more samples (routine, repeat or Hiturb) per month.
___ When a positive Total Coliform sample is positive for E. Coli and a repeat Total Coliform positive, OR, when a positive Total Coliform
sample is negative for E. Coli, but the repeat Total Coliform sample is positive and also is positive for E. Coli.
**Must collect a minimum of five (5) routine samples during the month following a repeat sample collection.

## REP PG3
©Copyright 1992-95, WindowChem Software, Inc., All Rights Reserved., (707) 864-0845, Revision 3.0
NEW YORK STATE DEPARTMENT OF HEALTH | [20 empty] | Water Systems Operation Report
Bureau of Public Water Supply Protection
SURFACE WATER SYSTEMS
Instructions: Complete form and submit to your local health unit within 10 days of the close of the reporting month.
NAME OF PUBLIC WATER SYSTEM |  |  | PROGRAM CODE |  |  |  | STATION | [8 empty] | REPORTING MONTH/YEAR
New Castle Consolidated WD |  |  |  | 1 | 0 | 0 |  | 5 | 9 | 0 | 3 | 4 | 4 | 2 |  |  | 0 | 4 | 2 | 2
Location | Millwood | [7 empty] | County |  |  | Westchester
(C,V,T)
Did an emergency occur in any part of the water system? | [16 empty] | Yes |  | No | x
Did source water bypass a process or were any of the processes inoperative or not operating | [16 empty] | Yes |  | No | x
as designed to modified to operate?
Were the pressure problems in the distribution system? | [16 empty] | Yes |  | No | x
Indicate name of sources used during the month:
Surface sources (s) |  |  |  | NYCDEP Catskill Aqueduct
Ground source(s)
Sample taken at |  |  |  | Millwood Pumping Station | [9 empty] | entry point to the distribution system.
NAME OF ENTRY POINT
The maximum allowable turbidity limit for the point of entry is | [9 empty] | 0.3 |  | NTUs.
1. Were daily turbidity analyses performed by the nephelometric method? | [13 empty] | Yes | x | No
2. Did a single repeat sample confirm that the maximum allowable turbidity | [15 empty] | DATE |  |  |  |  | No | x
limit has been exceeded? | [13 empty] | Yes
3. Did the turbidity, based on an average (and rounded to the nearest whole | [13 empty] | Yes |  | MCL DATE |  |  |  |  | No | x
number) for two consecutive days, exceed five turbidity?
4. Did the turbidity, as determined by a monthly average ( and rounded to the | [13 empty] | Yes |  | MCL DATE |  |  |  |  | No | x
nearest whole number) exceed the maximum allowable turbidity limit?
COMMENTS and/or REMARKS
Forms by EnviroWin (312-244-1900)
Reported by |  | John M. Young | [13 empty] | Date
Title | Chief Operator |  |  | Signature | [12 empty] | Cert. No. |  |  | NY0032778

## REP PG4
©Copyright 1992-95, WindowChem Software, Inc., All Rights Reserved., (707) 864-0845, Revision 3.0
NEW YORK STATE DEPARMENT OF HEALTH
DAILY OPERATION RECORD for this month of |  |  |  |  | 2022-04-01
Catskill Aqueduct / New Croton
Distribution Turbidity Results
| Amount of | Amount of | Raw | Chemicals | Post Chlorination | [6 empty] | Finished Water Turbidity |  |  |  | Date |  | Free
| of Raw | of Raw | Water | [11 empty] | Sample Location | Sample | Turbidity | Chlorine
| Water | Water | Turbidity |  | Gaseous |  |  |  |  | Liquid | Free |  |  |  |  | Taken |  | Residual
| (Catskill) | (Croton) |  | Alum | #1 | #2 | #3 | #4 | Chlorine | Hypo- | Chlorine | Finish | Pump | Two |  |  |  | mg/l
DATE | 1,000 Gals. | 1,000 Gals. |  | lbs. per | Weight | Weight | Weight | Weight | used | chlorite | Residual | Water | Station | consec. | Town Hall | 1 | 0.034 | 1.04
| Per Day | Per Day |  | 24 hrs. | of | of | of | of | lbs. per | used | mg/l | Turbidity. | Turbidity | day | Bedford | 2 | 0.033 | 1.16
[5 empty] | cylinders | cylinders | cylinders #2 | cylinders #2 | 24. hrs | qts. |  |  |  | aver. | Mobil | 3 | 0.045 | 0.93
1 | 2592 | 0 |  |  | 150 | 150 | 16.4 | 0 | 19.6 |  | 1.2967 |  | 0.0295 |  | Red Oak | 4 | 0.044 | 0.95
2 | 2513 | 0 |  |  | 146.8 | 150 | 0 | 0 | 33 |  | 1.32 |  | 0.0245 |  | campfire rd. | 5 | 0.036 | 0.94
3 | 2488 | 0 |  |  | 113.8 | 150 | 0 | 0 | 31.2 |  | 1.3233 |  | 0.026167 |  | DPW | 6 | 0.038 | 0.97
4 | 2442 | 0 |  |  | 82.6 | 150 | 0 | 0 | 29.2 |  | 1.28 |  | 0.027 |  | Shingle House Road | 7 | 0.039 | 1.26
5 | 2173 | 411 |  |  | 53.4 | 150 | 0 | 0 | 30.8 |  | 1.28 |  | 0.0295 |  | Town Hall | 8 | 0.035 | 1.09
6 | 2683 | 0 |  |  | 22.6 | 150 | 0 | 0 | 29.8 |  | 1.3167 |  | 0.029667 |  | Bedford | 9 | 0.033 | 1.01
7 | 2074 | 0 |  |  | 0 | 142.8 | 0 | 0 | 32.2 |  | 1.345 |  | 0.027 |  | Mt. Peak | 10 | 0.031 | 0.66
8 | 2511 | 0 |  |  | 0 | 110.6 | 0 | 0 | 29.6 |  | 1.3 |  | 0.036 |  | Red Oak | 11 | 0.067 | 1.11
9 | 2520 | 0 |  |  | 0 | 81 | 150 | 150 | 31.6 |  | 1.205 |  | 0.035167 |  | campfire rd. | 12 | 0.026 | 1.01
10 | 2953 | 0 |  |  | 0 | 49.4 | 150 | 150 | 28.2 |  | 1.23 |  | 0.0265 |  | DPW | 13 | 0.047 | 0.91
11 | 2363 | 0 |  |  | 0 | 21.2 | 150 | 150 | 26.6 |  | 1.2417 |  | 0.0245 |  | Shingle House Road | 14 | 0.035 | 1.12
12 | 2226 | 0 |  |  | 0 | 0 | 150.6 | 150 | 26.2 |  | 1.195 |  | 0.023 |  | Town Hall | 15 | 0.092 | 1.06
13 | 2425 | 0 |  |  | 0 | 0 | 124.4 | 150 | 25.2 |  | 1.1833 |  | 0.026333 |  | Bedford | 16 | 0.036 | 1.01
14 | 2105 | 0 |  |  | 0 | 0 | 99.2 | 150 | 33.2 |  | 1.27 |  | 0.034167 |  | Mt. Peak | 17 | 0.091 | 0.83
15 | 2636 | 0 |  |  | 150 | 150 | 66 | 150 | 26.2 |  | 1.2267 |  | 0.034667 |  | Red Oak | 18 | 0.039 | 0.83
16 | 2440 | 0 |  |  | 150 | 150 | 39.8 | 150 | 28 |  | 1.2017 |  | 0.037 |  | campfire rd. | 19 | 0.049 | 0.97
17 | 2961 | 0 |  |  | 146.8 | 144.2 | 11.8 | 143.8 | 29.4 |  | 1.2217 |  | 0.041333 |  | DPW | 20 | 0.031 | 0.8
18 | 2806 | 0 |  |  | 126.2 | 144.2 | 3 | 143.8 | 31.2 |  | 1.2033 |  | 0.027667 |  | Shingle House Road | 21 | 0.043 | 1.18
19 | 2507 | 0 |  |  | 95 | 144.2 | 3 | 143.8 | 25.6 |  | 1.2117 |  | 0.035 |  | Town Hall | 22 | 0.029 | 1.01
20 | 2029 | 0 |  |  | 69.4 | 144.2 | 3 | 143.8 | 29.8 |  | 1.2017 |  | 0.027667 |  | Bedford | 23 | 0.043 | 0.92
21 | 2990 | 0 |  |  | 39.6 | 144.2 | 0 | 143.8 | 27.6 |  | 1.1717 |  | 0.034167 |  | Mt. Peak | 24 | 0.078 | 0.72
22 | 2657 | 0 |  |  | 12 | 144.2 | 0 | 143.8 | 27.2 |  | 1.17 |  | 0.0295 |  | Red Oak | 25 | 0.026 | 0.81
23 | 3226 | 0 |  |  | -4 | 133 | 0 | 143.8 | 30.6 |  | 1.1933 |  | 0.028333 |  | campfire rd. | 26 | 0.04 | 0.94
24 | 2638 | 0 |  |  | 0 | 102.4 | 0 | 146 | 29 |  | 1.1983 |  | 0.025667 |  | DPW | 27 | 0.052 | 0.73
25 | 2890 | 0 |  |  | 0 | 73.4 | 0 | 146 | 28.6 |  | 1.195 |  | 0.030833 |  | Shingle House Road | 28 | 0.049 | 1.07
26 | 2751 | 0 |  |  | 0 | 44.8 | 0 | 146 | 32.4 |  | 1.1883 |  | 0.031 |  | Town Hall | 29 | 0.029 | 0.9
27 | 2353 | 0 |  |  | 0 | 12.4 | 0 | 146 | 32.4 |  | 1.1783 |  | 0.029167 |  | Bedford | 30 | 0.031 | 0.98
28 | 2719 | 0 |  |  | 0 | 0 | 0 | 137.2 | 31.6 |  | 1.1983 |  | 0.030167
29 | 2932 | 0 |  |  | 150 | 150 | 0 | 105.6 | 30.6 |  | 1.135 |  | 0.030667
30 | 2913 | 0 |  |  | 150 | 150 | 0 | 75 | 32.8 |  | 1.175 |  | 0.036167 |  | AVERAGE |  | 0.043367
31
Total | 77516 | 411 |  |  | 1654.2 |  |  |  | 879.4
Aver. | 2583.8667 | 13.7 |  |  | 55.14 |  |  |  | 29.3133 |  | 1.2286 |  | 0.030267
DOH-1015 (1/91) P. 2 OF 2

## O3CT
Millwood Water Treatment Plant
Monthly CT Monitoring Report
Month
Year | 2000
DATA INPUT | [9 empty] | DATA OUTPUT
ALL PARAMETERS REPORTED AT PEAK HOUR FLOW | [9 empty] | DO NOT INPUT DATA IN THIS TABLE
| [a] |  |  |  |  | Stage 1 | Stage 2 | Stage 3
[6 empty] | Ozone | Ozone | Ozone
| Peak Hourly | # of Ozone | Ozone | Ozone | Ozone | Residual | Residual | Residual | Raw | Actual CT Provided (min*mg/L*T10/T)
| Raw Water | Contactors | Applied to | Applied to | Applied to | Leaving | Leaving | Leaving | Water | [b] | [c] [d] | [c] [d] | Required | CT
| Flow | In Service | Stage 1 | Stage 2 | Stage 3 | Contactor | Contactor | Contactor | Temp. | Stage 1 | Stage 2 | Stage 3 | 1 log Giardia | Fraction | Compliance
Date | MGD | (1 or 2) | (Yes or No) | (Yes or No) | (Yes or No) | mg/L | mg/L | mg/L | deg. C | Contactor | Contactor | Contactor | (min*mg/L) | Achieved | Yes/No
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Average
Maximum
Minimum
(a) CT calculation shall be determined for PEAK HOUR RAW WATER FLOW each day.
Thus, the raw water quality data and ozone residual data input into this table shall be from that hour
during the day in which the raw water flowrate was greatest.
[b] If Ozone residual is < or = 0.3 mg/L, no credit is given, if the Ozone residual is > 0.3 mg/L, a 1/2 log credit is earned at the raw water temperature.
This model assumes ozone will always be added to the 1st stage.
[c] If Ozone is applied C = C/2, otherwise C = C
[d] Contactor T10/T = |  | 0.53

## CT1
1 Log Giardia Inactivation for Ozone
Data from the |  | Calculated |  | % Diff
Compliance Manual |  | Required | Temp | from
|  | CT |  | Manual
Y Data | X Data | 0.97 | 1 | -0.01
CT | Temp | 0.91 | 2
0.97 | 1 | 0.85 | 3
0.63 | 5 | 0.79 | 4
0.48 | 10 | 0.74 | 5 | 15.03
0.32 | 15 | 0.69 | 6
0.24 | 20 | 0.65 | 7
0.16 | 25 | 0.61 | 8
|  | 0.57 | 9
|  | 0.53 | 10 | 10.23
Best Fit Equation: |  | 0.5 | 11
y = 0.9781e^(-0.0723x) |  | 0.47 | 12
|  | 0.44 | 13
Calculated Required CT Eq.: |  | 0.42 | 14
y = (0.9781e^(-0.0723x))+0.06 |  | 0.39 | 15 | 18.1
|  | 0.37 | 16
|  | 0.35 | 17
e = 2.718 |  | 0.33 | 18
|  | 0.31 | 19
|  | 0.29 | 20 | 17.35
|  | 0.27 | 21
|  | 0.26 | 22
|  | 0.25 | 23
|  | 0.23 | 24
|  | 0.22 | 25 | 27.44

## FILT 1&2
NEW YORK STATE DEPARTMENT OF HEALTH | [12 empty] | Water Systems Operation Report
Bureau of Public Water Supply Protection
Instructions: Complete form and submit to your local health unit within 10 days of the close of the reporting month. | [12 empty] | FILTERED SURFACE WATER SYSTEMS
continuation sheet
FILTER EFFLUENT TURBIDITY NO. 1 | [6 empty] | FILTER EFFLUENT TURBIDITY NO. 2
DATE | 0 | 400 | 800 | 1200 | 1600 | 2000 | DATE | 0 | 400 | 800 | 1200 | 1600 | 2000
1 | [6 empty] | 1
2 | [6 empty] | 2
3 | [6 empty] | 3
4 | [6 empty] | 4
5 | [6 empty] | 5
6 | [6 empty] | 6
7 | [6 empty] | 7
8 | [6 empty] | 8
9 | [6 empty] | 9
10 | [6 empty] | 10
11 | [6 empty] | 11
12 | [6 empty] | 12
13 | [6 empty] | 13
14 | [6 empty] | 14
15 | [6 empty] | 15
16 | [6 empty] | 16
17 | [6 empty] | 17
18 | [6 empty] | 18
19 | [6 empty] | 19
20 | [6 empty] | 20
21 | [6 empty] | 21
22 | [6 empty] | 22
23 | [6 empty] | 23
24 | [6 empty] | 24
25 | [6 empty] | 25
26 | [6 empty] | 26
27 | [6 empty] | 27
28 | [6 empty] | 28
29 | [6 empty] | 29
30 | [6 empty] | 30
31 | [6 empty] | 31
Total No. Measurements_____________________________ | [6 empty] | Total No. Measurements_____________________________
Total No. above Perf. Std.____________________________ | [6 empty] | Total No. above Perf. Std.____________________________
Any measurements above 5 NTU? If yes, please note on | [6 empty] | Any measurements above 5 NTU? If yes, please note on
|  |  |  | DOH-3634 | [6 empty] | DOH-3634
DOH-3634

## FILT 5&6
FILTER EFFLUENT TURBIDITY |  |  |  | NAME OF PUBLIC |  |  | PROGRAM |  | FEDERAL ID |  |  | REPORTING
MONITORING |  |  |  | WATER SYSTEM |  |  | CODE |  | NUMBER |  |  | MONTH/YEAR
|  |  |  | New Castle Consolidated WD |  |  | 100 |  | 5903442
FILTER EFFLUENT TURBIDITY NO. 5 | [6 empty] | FILTER EFFLUENT TURBIDITY NO. 6
DATE | 0 | 400 | 800 | 1200 | 1600 | 2000 | DATE | 0 | 400 | 800 | 1200 | 1600 | 2000
1 | [6 empty] | 1
2 | [6 empty] | 2
3 | [6 empty] | 3
4 | [6 empty] | 4
5 | [6 empty] | 5
6 | [6 empty] | 6
7 | [6 empty] | 7
8 | [6 empty] | 8
9 | [6 empty] | 9
10 | [6 empty] | 10
11 | [6 empty] | 11
12 | [6 empty] | 12
13 | [6 empty] | 13
14 | [6 empty] | 14
15 | [6 empty] | 15
16 | [6 empty] | 16
17 | [6 empty] | 17
18 | [6 empty] | 18
19 | [6 empty] | 19
20 | [6 empty] | 20
21 | [6 empty] | 21
22 | [6 empty] | 22
23 | [6 empty] | 23
24 | [6 empty] | 24
25 | [6 empty] | 25
26 | [6 empty] | 26
27 | [6 empty] | 27
28 | [6 empty] | 28
29 | [6 empty] | 29
30 | [6 empty] | 30
31 | [6 empty] | 31
Total No. Measurements_____________________________ | [6 empty] | Total No. Measurements_____________________________
Total No. above Perf. Std.____________________________ | [6 empty] | Total No. above Perf. Std.____________________________
Any measurements above 5 NTU? If yes, please note on | [6 empty] | Any measurements above 5 NTU? If yes, please note on
|  |  |  | DOH-3634 | [6 empty] | DOH-3634
DOH-3634

## FILT 3&4
FILTER EFFLUENT TURBIDITY |  |  |  | NAME OF PUBLIC |  |  | PROGRAM |  | FEDERAL ID |  |  | REPORTING
MONITORING |  |  |  | WATER SYSTEM |  |  | CODE |  | NUMBER |  |  | MONTH/YEAR
|  |  |  | New Castle Consolidated WD |  |  | 100 |  | 5903442
FILTER EFFLUENT TURBIDITY NO. 3 | [6 empty] | FILTER EFFLUENT TURBIDITY NO. 4
DATE | 0 | 400 | 800 | 1200 | 1600 | 2000 | DATE | 0 | 400 | 800 | 1200 | 1600 | 2000
1 | [6 empty] | 1
2 | [6 empty] | 2
3 | [6 empty] | 3
4 | [6 empty] | 4
5 | [6 empty] | 5
6 | [6 empty] | 6
7 | [6 empty] | 7
8 | [6 empty] | 8
9 | [6 empty] | 9
10 | [6 empty] | 10
11 | [6 empty] | 11
12 | [6 empty] | 12
13 | [6 empty] | 13
14 | [6 empty] | 14
15 | [6 empty] | 15
16 | [6 empty] | 16
17 | [6 empty] | 17
18 | [6 empty] | 18
19 | [6 empty] | 19
20 | [6 empty] | 20
21 | [6 empty] | 21
22 | [6 empty] | 22
23 | [6 empty] | 23
24 | [6 empty] | 24
25 | [6 empty] | 25
26 | [6 empty] | 26
27 | [6 empty] | 27
28 | [6 empty] | 28
29 | [6 empty] | 29
30 | [6 empty] | 30
31 | [6 empty] | 31
Total No. Measurements_____________________________ | [6 empty] | Total No. Measurements_____________________________
Total No. above Perf. Std.____________________________ | [6 empty] | Total No. above Perf. Std.____________________________
Any measurements above 5 NTU? If yes, please note on | [6 empty] | Any measurements above 5 NTU? If yes, please note on
|  |  |  | DOH-3634 | [6 empty] | DOH-3634
DOH-3634

## T.O.C.
Total Organic Carbons |  |  |  | February 2020
Take sample every Monday
code:2640
units - cm-1
Month: | Raw Water | Floated Water | Filtered | % Removal from D.A.F. | % Removal from filtration | Total % Removal
1st Week | 2 | 1.92 | 1.27 | 4% | 33.8542 | 36.5
2nd Week | 2.1 | 1.37 | 1.14 | 34.76% | 16.7883 | 45.7143
3rd Week | 2.29 | 2.01 | 1.25 | 12.23% | 37.8109 | 45.4148
4th Week | 2.05 | 1.42 | 0.829 | 30.73% | 41.6197 | 59.561
(5th) Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Turbidity-NTU | Raw Water NTU | Floated Water NTU | Filtered | % Removal from D.A.F. | % Removal from filtration | Total % Removal
1st Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2nd Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3rd Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
4th Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
(5th) Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!

## CT1-2
1/2 Log Giardia Inactivation for Ozone
Data from the |  | Calculated |  | % Diff
Compliance Manual |  | Required | Temp | from
|  | CT |  | Manual
Y Data | X Data | 0.45 | 1 | -6.51
CT | Temp | 0.42 | 2
0.48 | 1 | 0.39 | 3
0.32 | 5 | 0.36 | 4
0.23 | 10 | 0.34 | 5 | 5.3
0.16 | 15 | 0.31 | 6
0.12 | 20 | 0.29 | 7
0.08 | 25 | 0.27 | 8
|  | 0.25 | 9
|  | 0.24 | 10 | 2.44
Best Fit Equation: |  | 0.22 | 11
y = 0.4843e^(-0.072x) |  | 0.2 | 12
|  | 0.19 | 13
|  | 0.18 | 14
|  | 0.16 | 15 | 2.73
|  | 0.15 | 16
|  | 0.14 | 17
|  | 0.13 | 18
|  | 0.12 | 19
|  | 0.11 | 20 | -4.56
|  | 0.11 | 21
|  | 0.1 | 22
|  | 0.09 | 23
|  | 0.09 | 24
|  | 0.08 | 25 | 0.09

## DOH4303-1
New York State Department of Health | [5 empty] | Water System Operation Report
Bureau of Public Water Supply Protection
FILTERED SURFACE WATER SYSTEMS
Instructions: Complete pages 1 and 2 of this form and submit to your local health department within 10 days of the close of the reporting month.
Complete page 3 if your system utilizes conventional or direct filtration and can answer "YES" to any of the four questions on page 3.
Public Water System Name |  |  |  | Reporting Month/Year |  |  | Type of Filtration
New Castle Consolidate WD |  |  |  | 2022-04-01 |  |  | Conventional |  |  | Direct
Public Water System ID # |  |  |  | Town, Village,or City |  | County | Alternative |  |  | Slow Sand
NY | 5903442 |  |  | Millwood |  | Westchester | Diatom Earth
| Entry Point Chlorine Residual (mg/L) | [5 empty] | Distribution System Turbidity Results
Date | 0000 | 0400 | 0800 | 1200 | 1600 | 2000 | Sample Location |  |  |  | (NTU)
1 | 1.27 | 1.25 | 1.24 | 1.24 | 1.3 | 1.36 | Town Hall |  |  |  | 0.034
2 | 1.28 | 1.29 | 1.33 | 1.28 | 1.33 | 1.27 | Bedford |  |  |  | 0.033
3 | 1.33 | 1.29 | 1.31 | 1.32 | 1.34 | 1.33 | Mt. Peak |  |  |  | 0.045
4 | 1.34 | 1.34 | 1.35 | 1.24 | 1.34 | 1.33 | Red Oak |  |  |  | 0.044
5 | 1.32 | 1.3 | 1.3 | 1.31 | 1.16 | 1.29 | campfire rd. |  |  |  | 0.036
6 | 1.28 | 1.29 | 1.3 | 1.32 | 1.35 | 1.36 | DPW |  |  |  | 0.038
7 | 1.35 | 1.36 | 1.29 | 1.37 | 1.29 | 1.41 | Shingle House Road |  |  |  | 0.039
8 | 1.29 | 1.23 | 1.34 | 1.33 | 1.39 | 1.22 | Town Hall |  |  |  | 0.035
9 | 1.16 | 1.21 | 1.19 | 1.24 | 1.2 | 1.23 | Bedford |  |  |  | 0.033
10 | 1.2 | 1.3 | 1.19 | 1.21 | 1.25 | 1.23 | Mt. Peak |  |  |  | 0.031
11 | 1.25 | 1.23 | 1.24 | 1.24 | 1.24 | 1.25 | Red Oak |  |  |  | 0.067
12 | 1.24 | 1.23 | 1.12 | 1.22 | 1.16 | 1.2 | campfire rd. |  |  |  | 0.026
13 | 1.19 | 1.18 | 1.2 | 1.17 | 1.19 | 1.17 | DPW |  |  |  | 0.047
14 | 1.2 | 1.19 | 1.21 | 1.32 | 1.41 | 1.29 | Shingle House Road |  |  |  | 0.035
15 | 1.24 | 1.17 | 1.24 | 1.23 | 1.15 | 1.33 | Town Hall |  |  |  | 0.092
16 | 1.16 | 1.2 | 1.23 | 1.2 | 1.16 | 1.26 | Bedford |  |  |  | 0.036
17 | 1.16 | 1.27 | 1.2 | 1.23 | 1.24 | 1.23 | Mt. Peak |  |  |  | 0.091
18 | 1.24 | 1.23 | 1.22 | 1.18 | 1.16 | 1.19 | Red Oak |  |  |  | 0.039
19 | 1.19 | 1.2 | 1.17 | 1.2 | 1.26 | 1.25 | campfire rd. |  |  |  | 0.049
20 | 1.26 | 1.27 | 1.2 | 1.21 | 1.14 | 1.13 | DPW |  |  |  | 0.031
21 | 1.1 | 1.19 | 1.14 | 1.18 | 1.14 | 1.28 | Shingle House Road |  |  |  | 0.043
22 | 1.08 | 1.15 | 1.21 | 1.18 | 1.21 | 1.19 | Town Hall |  |  |  | 0.029
23 | 1.15 | 1.2 | 1.15 | 1.24 | 1.2 | 1.22 | Bedford |  |  |  | 0.043
24 | 1.22 | 1.26 | 1.2 | 1.16 | 1.16 | 1.19 | Mt. Peak |  |  |  | 0.078
25 | 1.24 | 1.22 | 1.21 | 1.17 | 1.15 | 1.18 | Red Oak |  |  |  | 0.026
26 | 1.19 | 1.2 | 1.18 | 1.19 | 1.18 | 1.19 | campfire rd. |  |  |  | 0.04
27 | 1.17 | 1.19 | 1.16 | 1.18 | 1.17 | 1.2 | DPW |  |  |  | 0.052
28 | 1.24 | 1.17 | 1.19 | 1.2 | 1.15 | 1.24 | Shingle House Road |  |  |  | 0.049
29 | 1.06 | 1.11 | 1.16 | 1.15 | 1.14 | 1.19 | Town Hall |  |  |  | 0.029
30 | 1.08 | 1.16 | 1.16 | 1.21 | 1.2 | 1.24 | Bedford |  |  |  | 0.031
31
[7 empty] | Monthly Turbidity Average: |  |  |  | 0.043367
Location of Entry Point: |  |  | Pump Station Sink
Population Served: |  |  | 16800
Entry Point Disinfection Monitoring: | [6 empty] | If Grab, number of samples per day: |  |  |  | 6
Monitoring Results:
Did the Entry Point residual fall below 0.2 mg/L for more than 4 hours ? | [6 empty] | ……………………………………………………………………
Did the monthly average of the distribution system turbidity results exceed 5 NTU? ………………………………
Reported by (print name): |  |  | John M. Young |  |  |  |  | Title: | Chief Operator
NYSDOH Operator Certification Number : NY |  |  |  |  | 32778 |  | Operator Grade Level: |  | IA
Signature: | [7 empty] | Date:
DOH-4303 (1/05) Page 1 of 3

## DOH4303-2
Compostite Filter Effluent Monitoring
| Date | Results (NTU)
|  | 0000 | 0400 | 0800 | 1200 | 1600 | 2000
| 1 | 0.025 | 0.027 | 0.034 | 0.024 | 0.027 | 0.027
| 2 | 0.026 | 0.026 | 0.027 | 0.035 | 0.031 | 0.024
| 3 | 0.022 | 0.023 | 0.025 | 0.026 | 0.02 | 0.025
| 4 | 0.024 | 0.027 | 0.026 | 0.026 | 0.024 | 0.028
| 5 | 0.027 | 0.029 | 0.028 | 0.024 | 0.026 | 0.025
| 6 | 0.024 | 0.029 | 0.024 | 0.027 | 0.03 | 0.026
| 7 | 0.023 | 0.029 | 0.028 | 0.029 | 0.028 | 0.031
| 8 | 0.034 | 0.031 | 0.025 | 0.028 | 0.032 | 0.035
| 9 | 0.032 | 0.037 | 0.031 | 0.023 | 0.032 | 0.035
| 10 | 0.029 | 0.034 | 0.025 | 0.029 | 0.018 | 0.029
| 11 | 0.024 | 0.027 | 0.028 | 0.031 | 0.024 | 0.027
| 12 | 0.024 | 0.019 | 0.027 | 0.019 | 0.029 | 0.023
| 13 | 0.027 | 0.022 | 0.023 | 0.025 | 0.028 | 0.029
| 14 | 0.027 | 0.029 | 0.035 | 0.038 | 0.036 | 0.035
| 15 | 0.036 | 0.034 | 0.036 | 0.024 | 0.023 | 0.03
| 16 | 0.035 | 0.025 | 0.034 | 0.033 | 0.031 | 0.031
| 17 | 0.037 | 0.034 | 0.032 | 0.032 | 0.032 | 0.029
| 18 | 0.029 | 0.03 | 0.035 | 0.024 | 0.033 | 0.03
| 19 | 0.03 | 0.032 | 0.038 | 0.026 | 0.02 | 0.02
| 20 | 0.03 | 0.027 | 0.028 | 0.028 | 0.025 | 0.027
| 21 | 0.029 | 0.028 | 0.033 | 0.033 | 0.032 | 0.035
| 22 | 0.013 | 0.028 | 0.034 | 0.036 | 0.029 | 0.033
| 23 | 0.035 | 0.035 | 0.026 | 0.026 | 0.025 | 0.024
| 24 | 0.029 | 0.03 | 0.029 | 0.028 | 0.023 | 0.024
| 25 | 0.024 | 0.027 | 0.022 | 0.027 | 0.029 | 0.027
| 26 | 0.03 | 0.026 | 0.028 | 0.033 | 0.034 | 0.034
| 27 | 0.019 | 0.022 | 0.023 | 0.028 | 0.029 | 0.025
| 28 | 0.036 | 0.036 | 0.026 | 0.032 | 0.024 | 0.03
| 29 | 0.031 | 0.026 | 0.025 | 0.024 | 0.03 | 0.035
| 30 | 0.031 | 0.034 | 0.034 | 0.028 | 0.039 | 0.037
31
Required monitoring frequency:
If continuous, did equipment failure require grab sampling for more than 5 working days?
Total number of analyses: | 180 |  | Number of analyses that exceeded the performance standard 1: |  |  |  |  | 0
Percentage of analyses that exceeded the performance standard 1: |  |  |  |  | 0 | %
Did any analyses exceed the maximum turbidity standard 2? …………………………………………………..
Individual Filter Effluent Turbidity Monitoring (Complete if filtration type is conventional or direct)
Was individual filter effluent turbidity monitoring conducted during the last month?
Did failure of continuous monitoring equipment require grab sampling for more than 5 working days?
Comments:
1 Performance Standards: 0.3 NTU for conventional and direct filtration; 1.0 NTU for slow sand and D.E.; 1.0 NTU or value set by the Department for
alternative filtration
2 Maximum allowable turbidity standards: 1 NTU for conventional and direct filtration; 5 NTU for slow sand and D.E.;5 NTU or value set by the Department
for alternative filtration.
DOH-4303 (1/05) Page 2 of 3

## DOH4303-3
INDIVIDUAL FILTER EFFLUENT TURBIDITY MONITORING
Instructions: Complete this page and attach it to your operation report if you utilize conventional or direct filtration and can answer "YES" to any of
the four questions below.
1. Did any filter(s) exceed 1.0 NTU in two consecutive readings taken 15 minutes apart? ………………………………………………….
If yes report the filter number(s), corresponding date(s), and the turbidity value(s) which exceeded 1.0 NTU during the
month (only for filters that had two consecutive readings exceeding 1.0 NTU), and the reason for abnormal filter
performance. If an obvious reason cannot be identified, a filter profile must be submitted within 7 days of exceedance.
| Filter Number: |  |  |  | Filter Number: |  |  | Filter Number:
| Date | Time | (NTU) |  | Date | Time | (NTU) | Date | Time | (NTU)
2. Did any filter exceed 1.0 NTU in two consecutive readings taken 15 minutes apart at any time
in each of the last 3 consecutive months? ………………………………………………………………
If "YES" a self-assessment of the filter must be conducted by the system. The system should conduct the assessment within 14 days of the exceedance and submit
the self-assessment to the Department. Report the filter number, the date the self-assessment was triggered, and the date it was completed.
Filter Number: |  |  |  | Trigger date: |  |  |  | Completion date:
3. Did any filter exceed 2.0 NTU in two consecutive readings taken 15 minutes apart at any time
in each of the last 2 consecutive months? ……………………………………………………………
If yes a Comprehensive Performance Evaluation (CPE) is required. A copy of the CPE report must be submitted to the Department within 120 days of the trigger date.
Report the filter number that triggered CPE, and the date the CPE was triggered.
Filter Number: |  |  |  | Trigger date:
4. If the system serves > 10,000 persons, did any filter exceed 0.5 NTU in each of the first 2 consecutive
15 minute readings following the first 4 hours of continuous filter operation? ……................
If YES report the filter number, the date on which the exceedance occurred, and the turbidities of the 2 consecutive readings. Report the obvious reason for the abnormal
filter performance, or submit a filter profile within 7 days of the exceedance.
Filter Number: |  |  | Date: |  |  | Consecutive Readings: |  |  | NTU and: |  | NTU
Reason for abnormal filter performance:
Public Water System ID: NY |  |  | 5903442
Reported by (print name): |  |  | John M. Young |  |  |  |  | Title: | Chief Operator
NYSDOH Operator Certification Number:NY |  |  |  |  | 32778 |  |  | Operator Grade Level: |  | IA
Signature: | [7 empty] | Date:
DOH-4303 (1/05) Page 3 of 3

## DOH-360CFL-1
New York State Department of Health | [7 empty] | WATER SYSTEM OPERATION REPORT
Bureau of Water Supply Protection | [7 empty] | For Use By Public Water Systems that Treat with Chlorine and/or Fluoride
Public Water System Name |  |  |  | Reporting Month/Year |  |  |  |  | Date Report Submitted |  |  | Source Water Type(s)
New Castle Consolidate WD |  |  |  | 2022-04-01 |  |  |  |  | 2022-05-06
Public Water System ID |  |  |  | County |  |  |  |  | Town, Village or City
NY 5903442 |  |  |  | Westchester |  |  |  |  | Millwood
Treatment Plant(s) Identification : |  |  | #1 | [5 empty] | #2 |  |  | #3
Fluoride Compound Used:
Fluoride Residual Testing Method Used: |  |  |  | SPADNS
Fluoride Injection Point Location(s) Id: |  |  | #1 | [5 empty] | #2 |  |  | #3 | Pump Station
Date of Fluoride Split Sample: |  |  |  | 2022-04-05
DATE | Source(s) in use | Treated Water Volume (1,000/GPD.) |  | Chlorination | [6 empty] | Fluoridation |  |  | Other Treatments
|  |  |  | Gaseous |  |  |  |  | Liquid | Free chlorine residual at entry point (mg/l) | Fluoride Usage per day (gallons) | Fluoride Compound used per day (lbs) | Fluoride finished water (mgL) | Ortho-phosphate Gallons | Potassium Permanganate Lbs/day
|  |  |  | #1 Cylinder weight (lbs.) | #2 Cylinder weight (lbs.) | #3 Cylinder weight (lbs.) | #4 Cylinder weight (lbs.) | Chlorine used per day (lbs.) | Hypochlorite added to crock (gallons or quarts)
1 | Catskill Aqu. | 2591 |  | 150 | 150 | 16.4 | 0 | 19.6 |  | 1.2767 |  | 16.177 | 0.695 | 7 | 0
2 | Catskill Aqu. | 2535 |  | 146.8 | 150 | 0 | 0 | 33 |  | 1.2967 |  | 16.177 | 0.70833 | 8 | 0
3 | Catskill Aqu. | 2475 |  | 113.8 | 150 | 0 | 0 | 31.2 |  | 1.32 |  | 17.3325 | 0.72333 | 7.5 | 0
4 | Catskill Aqu. | 2459 |  | 82.6 | 150 | 0 | 0 | 29.2 |  | 1.3233 |  | 16.177 | 0.71667 | 8 | 0
5 | Catskill & Croton | 2646 |  | 53.4 | 150 | 0 | 0 | 30.8 |  | 1.28 |  | 17.3325 | 0.68333 | 8 | 0
6 | Catskill Aqu. | 2692 |  | 22.6 | 150 | 0 | 0 | 29.8 |  | 1.3167 |  | 18.488 | 0.605 | 8 | 0
7 | Catskill Aqu. | 2041 |  | 0 | 142.8 | 0 | 0 | 32.2 |  | 1.345 |  | 17.3325 | 0.725 | 8 | 0
8 | Catskill Aqu. | 2597 |  | 0 | 110.6 | 0 | 0 | 29.6 |  | 1.3 |  | 17.3325 | 0.755 | 8 | 0
9 | Catskill Aqu. | 2518 |  | 0 | 81 | 150 | 150 | 31.6 |  | 1.205 |  | 17.3325 | 0.71333 | 8 | 0
10 | Catskill Aqu. | 2961 |  | 0 | 49.4 | 150 | 150 | 28.2 |  | 1.23 |  | 16.177 | 0.68333 | 7.5 | 0
11 | Catskill Aqu. | 2405 |  | 0 | 21.2 | 150 | 150 | 26.6 |  | 1.2417 |  | 17.3325 | 0.63833 | 7.5 | 0
12 | Catskill Aqu. | 2292 |  | 0 | 0 | 150.6 | 150 | 26.2 |  | 1.195 |  | 17.3325 | 0.64667 | 7 | 0
13 | Catskill Aqu. | 2435 |  | 0 | 0 | 124.4 | 150 | 25.2 |  | 1.1833 |  | 18.488 | 0.73333 | 8 | 0
14 | Catskill Aqu. | 2149 |  | 0 | 0 | 99.2 | 150 | 33.2 |  | 1.27 |  | 20.799 | 0.75333 | 9 | 0
15 | Catskill Aqu. | 2688 |  | 150 | 150 | 66 | 150 | 26.2 |  | 1.2267 |  | 18.488 | 0.73833 | 8 | 0
16 | Catskill Aqu. | 2442 |  | 150 | 150 | 39.8 | 150 | 28 |  | 1.2017 |  | 20.799 | 0.77 | 8 | 0
17 | Catskill Aqu. | 3073 |  | 146.8 | 144.2 | 11.8 | 143.8 | 29.4 |  | 1.2217 |  | 20.799 | 0.76 | 8 | 0
18 | Catskill Aqu. | 2858 |  | 126.2 | 144.2 | 3 | 143.8 | 31.2 |  | 1.2033 |  | 20.799 | 0.61167 | 9 | 0
19 | Catskill Aqu. | 2530 |  | 95 | 144.2 | 3 | 143.8 | 25.6 |  | 1.2117 |  | 17.3325 | 0.615 | 7.5 | 0
20 | Catskill Aqu. | 2035 |  | 69.4 | 144.2 | 3 | 143.8 | 29.8 |  | 1.2017 |  | 19.6435 | 0.67167 | 9 | 0
21 | Catskill Aqu. | 3010 |  | 39.6 | 144.2 | 0 | 143.8 | 27.6 |  | 1.1717 |  | 20.799 | 0.72167 | 8 | 0
22 | Catskill Aqu. | 2704 |  | 12 | 144.2 | 0 | 143.8 | 27.2 |  | 1.17 |  | 20.799 | 0.75667 | 9 | 0
23 | Catskill Aqu. | 3216 |  | -4 | 133 | 0 | 143.8 | 30.6 |  | 1.1933 |  | 20.799 | 0.76333 | 9 | 0
24 | Catskill Aqu. | 2645 |  | 0 | 102.4 | 0 | 146 | 29 |  | 1.1983 |  | 18.488 | 0.77333 | 8 | 0
25 | Catskill Aqu. | 2954 |  | 0 | 73.4 | 0 | 146 | 28.6 |  | 1.195 |  | 20.799 | 0.78433 | 8 | 0
26 | Catskill Aqu. | 2781 |  | 0 | 44.8 | 0 | 146 | 32.4 |  | 1.1883 |  | 23.11 | 0.75167 | 9 | 0
27 | Catskill Aqu. | 2363 |  | 0 | 12.4 | 0 | 146 | 32.4 |  | 1.1783 |  | 23.11 | 0.75333 | 9 | 0
28 | Catskill Aqu. | 2722 |  | 0 | 0 | 0 | 137.2 | 31.6 |  | 1.1983 |  | 20.799 | 0.715 | 9.5 | 0
29 | Catskill Aqu. | 2954 |  | 150 | 150 | 0 | 105.6 | 30.6 |  | 1.135 |  | 16.177 | 0.69833 | 9.5 | 0
30 | Catskill Aqu. | 2929 |  | 150 | 150 | 0 | 75 | 32.8 |  | 1.175 |  | 21.9545 | 0.72 | 7 | 0
31
Total |  | 78700 | [5 empty] | 879.4 |  |  |  | 568.506 |  | 245
Average |  | 2623.3333 | [5 empty] | 29.3133 |  | 1.2284 |  | 18.9502 | 0.71281 | 8.1667
Chlorine Mix Ration = |  |  |  | quarts/gallons of | [5 empty] | %chlorine added to |  |  | gallons of water in crock
Reported by/Title: |  | John M. Young, Chief Operator | [7 empty] | NYSDOH Operator Certification Number |  |  |  | 32778
Signature: | [8 empty] | Date: |  |  | Operator Grade Level: |  |  | IA
DOH-360CFL (Rev. 10/04) page 1 of 2

## DOH-360CFL-2
Microbiological Samples and Free Chlorine Residual
Sample Location | Date of Sample | Sample Type | Total Coliform Positive |  | E-coli Positive | Free Chlorine Residual (mg/l) | Population Served: |  | 16800
[7 empty] | # of microbiological monitoring samples required: |  |  | 15
|  | 1. Routine 2. Repeat |  |  |  |  | Number of microbiological monitoring samples taken: |  |  | 16
Millwood Post Office, 230 Saw Mill River Road | 2022-04-01 | 1 |  |  |  | 1.2 | Did an M&R violation occur?
Bedford Road Pump Station, 438 Bedford Road | 2022-04-04 | 1 |  |  |  | 1.1 | If "Yes," Check Reason(s) below:
Ethical Society, 108 Pinesbridge Road | 2022-04-05 | 1 |  |  |  | 1.17
DPW Office, 280 Joan Corwin Way | 2022-04-07 | 1 |  |  |  | 0.99
Moutain Peak Pump Station, 17 Mountain Peak Road | 2022-04-08 | 1 |  |  |  | 0.91
Red Oak Pump Station, Next to 60 Red Oak Lane | 2022-04-11 | 1 |  |  |  | 1.01
Town Hall, 200 South Greeley Avenue | 2022-04-12 | 1 |  |  |  | 1.01 | Did an MCL violation occur?
Sample Station New Campfire Road and TSP | 2022-04-14 | 1 |  |  |  | 1.02 | If "Yes," check reason(s) below (see also Part 5, Table 6 for Additional information)
Sample Station, Carolyn Place and Bessel Lane | 2022-04-18 | 1 |  |  |  | 0.59
Art Center, 939 Hardscrabble Road | 2022-04-19 | 1 |  |  |  | 0.99
Sample Station, Route 100 and Shinglehouse Road | 2022-04-20 | 1 |  |  |  | 1.08
Sample Station Across from 2 Sunset Drive | 2022-04-21 | 1 |  |  |  | 1.27
Sample Station Near 6 Orchard Drive | 2022-04-22 | 1 |  |  |  | 0.93
Sample Station Across from 575 Old Bedford Road | 2022-04-25 | 1 |  |  |  | 0.89
Sample Station Near 186 Croton Lake Road | 2022-04-28 | 1 |  |  |  | 0.75
Chappaqua Post Office 107 North Greeley Avenue | 2022-04-29 | 1 |  |  |  | 0.87
Sample Collector | Town of New Castle DPW | [6 empty] | Date: | 4/4/22 - 4/29/22
Sample Collector | [7 empty] | Date:
Name of NYSDOH Certified Laboratory: |  |  |  | Westchester County Deparment of Labs and Research
Did any MCL violation occur? If so, please describe:
Did an emergency or low pressure problem occur?
Did source water bypass an existing treatment process in the system? | [7 empty] | If so, please explain:
Comments:
DOH-360CFL (Rev. 10/04) page 2 of 2