## chem
Month | 2023-04-01
Date | gal ortho | gal NAOH | GAL FLUR | lbs ortho | lbs NAOH | lbs Fluor | gal/hr PAC | lbs/day PAC | gal/hr poly | lbs/day poly | O3 lb/day | CL2 lb/day | kmno4 gal/hr | kmno4lbs/day | DATE
1 | 6 | 37.2 | 5 | 61.5 | 108.0288 | 11.555 | 1.99 | 491.928 | 12.2 | 4.8576 | 22.33 | 22.54 |  | 0 | 1
2 | 6 | 40.5 | 6 | 61.5 | 117.612 | 13.866 | 1.81 | 447.432 | 12.2 | 4.8576 | 21.11 | 21.68 |  | 0 | 2
3 | 6 | 43.2 | 6 | 61.5 | 125.4528 | 13.866 | 1.78 | 440.016 | 12.1 | 4.8177 | 21.65 | 21.32 |  | 0 | 3
4 | 7 | 41.25 | 6 | 71.75 | 119.79 | 13.866 | 1.73 | 427.656 | 12.1 | 4.8177 | 22.83 | 21.51 |  | 0 | 4
5 | 6 | 41.9 | 6 | 61.5 | 121.6776 | 13.866 | 1.77 | 437.544 | 12 | 4.7779 | 22.79 | 21.45 |  | 0 | 5
6 | 7 | 40.8 | 6 | 71.75 | 118.4832 | 13.866 | 1.81 | 447.432 | 12.1 | 4.8177 | 23.15 | 21.57 |  | 0 | 6
7 | 7 | 43.5 | 7 | 71.75 | 126.324 | 16.177 | 1.81 | 447.432 | 12.1 | 4.8177 | 22.97 | 26.4 |  | 0 | 7
8 | 7 | 44.55 | 7 | 71.75 | 129.3732 | 16.177 | 1.9 | 469.68 | 12.2 | 4.8576 | 24.08 | 30.72 |  | 0 | 8
9 | 8 | 45.1 | 7 | 82 | 130.9704 | 16.177 | 1.91 | 472.152 | 12.2 | 4.8576 | 23.31 | 30.25 |  | 0 | 9
10 | 8 | 57.3 | 8 | 82 | 166.3992 | 18.488 | 2.21 | 546.312 | 13.5 | 5.3752 | 29.36 | 36.36 |  | 0 | 10
11 | 8 | 45.1 | 7 | 82 | 130.9704 | 16.177 | 1.89 | 467.208 | 11.9 | 4.7381 | 31.16 | 28.1 |  | 0 | 11
12 | 10 | 66.6 | 9 | 102.5 | 193.4064 | 20.799 | 2.5 | 618 | 15.9 | 6.3307 | 29.61 | 39.83 |  | 0 | 12
13 | 9 | 57.3 | 8 | 92.25 | 166.3992 | 18.488 | 2.27 | 561.144 | 15.9 | 6.3307 | 27.88 | 36.95 |  | 0 | 13
14 | 11 | 73.35 | 10 | 112.75 | 213.0084 | 23.11 | 2.85 | 704.52 | 17.3 | 6.8882 | 33.31 | 48.05 |  | 0 | 14
15 | 7 | 50.1 | 7 | 71.75 | 145.4904 | 16.177 | 2.02 | 499.344 | 14.7 | 5.853 | 27.94 | 32.46 |  | 0 | 15
16 | 8 | 53.7 | 22.6 | 82 | 155.9448 | 52.2286 | 2.06 | 509.232 | 14 | 5.5742 | 27.39 | 34.07 |  | 0 | 16
17 | 8 | 54.75 | 7.5 | 82 | 158.994 | 17.3325 | 2.33 | 575.976 | 15.2 | 6.052 | 28.55 | 39.41 |  | 0 | 17
18 | 90 | 55.95 | 8 | 922.5 | 162.4788 | 18.488 | 2.13 | 526.536 | 13.2 | 5.2557 | 26.25 | 35.63 |  | 0 | 18
19 | 8 | 57.6 | 9 | 82 | 167.2704 | 20.799 | 2.11 | 521.592 | 14.4 | 5.7335 | 25.59 | 35.05 |  | 0 | 19
20 | 8 | 52.95 | 9 | 82 | 153.7668 | 20.799 | 2.48 | 613.056 | 16 | 6.3706 | 31.31 | 41 |  | 0 | 20
21 | 11 | 66.6 | 11 | 112.75 | 193.4064 | 25.421 | 2.6 | 642.72 | 16.7 | 6.6493 | 28.81 | 39.39 |  | 0 | 21
22 | 8 | 52.5 | 8 | 82 | 152.46 | 18.488 | 2.61 | 645.192 | 18.1 | 7.2067 | 31.99 | 38.85 |  | 0 | 22
23 | 7 | 45 | 7 | 71.75 | 130.68 | 16.177 | 1.71 | 422.712 | 13.2 | 5.2557 | 25.23 | 25.57 |  | 0 | 23
24 | 10 | 39.9 | 10 | 102.5 | 115.8696 | 23.11 | 2.39 | 590.808 | 14.7 | 5.853 | 28.2 | 34.83 |  | 0 | 24
25 | 7 | 46.5 | 8 | 71.75 | 135.036 | 18.488 | 2.32 | 573.504 | 15.1 | 6.0122 | 30.05 | 34.57 |  | 0 | 25
26 | 7.5 | 50.4 | 9 | 76.875 | 146.3616 | 20.799 | 2.13 | 526.536 | 12.8 | 5.0964 | 28.74 | 31.61 |  | 0 | 26
27 | 7.5 | 49.8 | 9 | 76.875 | 144.6192 | 20.799 | 2.11 | 521.592 | 12.8 | 5.0964 | 28.64 | 29.6 |  | 0 | 27
28 | 7.5 | 49.8 | 9.5 | 76.875 | 144.6192 | 21.9545 | 2.08 | 514.176 | 13.1 | 5.2159 | 30.36 | 32.76 |  | 0 | 28
29 | 6 | 38.85 | 7 | 61.5 | 112.8204 | 16.177 | 1.76 | 435.072 | 12 | 4.7779 | 28.88 | 31.41 |  | 0 | 29
30 | 8.5 | 46.95 | 7.5 | 87.125 | 136.3428 | 17.3325 | 1.77 | 437.544 | 9.8 | 3.902 | 29.83 | 33.44 |  | 0 | 30
31 |  |  |  | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | 0 | 31
Tot | 315 | 1489 | 247.1 | 3228.75 | 4324.056 | 571.0481 | 62.84 | 15534.048 | 409.5 | 163.0465 | 813.3 | 956.38 | 0 | 0 | Total
AVG | 10.5 | 49.6333 | 8.2367 | 104.1532 | 139.4857 | 18.4209 | 2.0947 | 517.8016 | 13.65 | 5.2596 | 27.11 | 31.8793 | #DIV/0! | 0 | Avg.
Date | Raw Water | Post NAOH | Corrosion | Flouride | Chlorine | PACL | KmnO4 | Polymer | Ozone | Raw Water | Raw Water | Pump
| /1,000 gal | lbs/day | Inhibitor | lbs/day | lbs/day | lbs/day | lbs/day | lbs/day | lbs/day | Temp oF | Turbidity | Station
|  |  | lbs/day | [8 empty] | pH
1 | 2211 | 108.0288 | 61.5 | 11.555 | 22.54 | 491.928 |  | 4.8576 | 22.33 | 43.81 | 1.52 | 7.5
2 | 2149 | 117.612 | 61.5 | 13.866 | 21.68 | 447.432 |  | 4.8576 | 21.11 | 43.25 | 1.47 | 7.4
3 | 2170 | 125.4528 | 61.5 | 13.866 | 21.32 | 440.016 |  | 4.8177 | 21.65 | 43.39 | 1.57 | 7.6
4 | 2118 | 119.79 | 71.75 | 13.866 | 21.51 | 427.656 |  | 4.8177 | 22.83 | 44.25 | 1.51 | 7.5
5 | 2246 | 121.6776 | 61.5 | 13.866 | 21.45 | 437.544 |  | 4.7779 | 22.79 | 45.38 | 1.5 | 7.6
6 | 2196 | 118.4832 | 71.75 | 13.866 | 21.57 | 447.432 |  | 4.8177 | 23.15 | 47.26 | 1.5 | 7.5
7 | 2194 | 126.324 | 71.75 | 16.177 | 26.4 | 447.432 |  | 4.8177 | 22.97 | 47.7 | 1.95 | 7.5
8 | 2443 | 129.3732 | 71.75 | 16.177 | 30.72 | 469.68 |  | 4.8576 | 24.08 | 47.44 | 1.71 | 7.5
9 | 2438 | 130.9704 | 82 | 16.177 | 30.25 | 472.152 |  | 4.8576 | 23.31 | 47.68 | 1.71 | 7.4
10 | 2795 | 166.3992 | 82 | 18.488 | 36.36 | 546.312 |  | 5.3752 | 29.36 | 48.38 | 1.84 | 7.5
11 | 2423 | 130.9704 | 82 | 16.177 | 28.1 | 467.208 |  | 4.7381 | 31.16 | 49.08 | 1.82 | 7.5
12 | 3212 | 193.4064 | 102.5 | 20.799 | 39.83 | 618 |  | 6.3307 | 29.61 | 51.48 | 1.79 | 7.5
13 | 2995 | 166.3992 | 92.25 | 18.488 | 36.95 | 561.144 |  | 6.3307 | 27.88 | 51.53 | 1.77 | 7.5
14 | 3873 | 213.0084 | 112.75 | 23.11 | 48.05 | 704.52 |  | 6.8882 | 33.31 | 51.76 | 1.87 | 7.7
15 | 2516 | 145.4904 | 71.75 | 16.177 | 32.46 | 499.344 |  | 5.853 | 27.94 | 53 | 1.81 | 7.6
16 | 2646 | 155.9448 | 82 | 52.2286 | 34.07 | 509.232 |  | 5.5742 | 27.39 | 52.83 | 1.96 | 7.6
17 | 3083 | 158.994 | 82 | 17.3325 | 39.41 | 575.976 |  | 6.052 | 28.55 | 51.02 | 1.85 | 7.6
18 | 2777 | 162.4788 | 922.5 | 18.488 | 35.63 | 526.536 |  | 5.2557 | 26.25 | 50.06 | 1.74 | 7.5
19 | 2693 | 167.2704 | 82 | 20.799 | 35.05 | 521.592 |  | 5.7335 | 25.59 | 50.53 | 1.9 | 7.5
20 | 3270 | 153.7668 | 82 | 20.799 | 41 | 613.056 |  | 6.3706 | 31.31 | 51.24 | 2.21 | 7.5
21 | 3380 | 193.4064 | 112.75 | 25.421 | 39.39 | 642.72 |  | 6.6493 | 28.81 | 51.77 | 2.05 | 7.4
22 | 3350 | 152.46 | 82 | 18.488 | 38.85 | 645.192 |  | 7.2067 | 31.99 | 52.47 | 1.97 | 7.4
23 | 2146 | 130.68 | 71.75 | 16.177 | 25.57 | 422.712 |  | 5.2557 | 25.23 | 52.86 | 1.85 | 7.4
24 | 3153 | 115.8696 | 102.5 | 23.11 | 34.83 | 590.808 |  | 5.853 | 28.2 | 52.24 | 2.04 | 7.5
25 | 2956 | 135.036 | 71.75 | 18.488 | 34.57 | 573.504 |  | 6.0122 | 30.05 | 53.05 | 1.98 | 7.4
26 | 2772 | 146.3616 | 76.875 | 20.799 | 31.61 | 526.536 |  | 5.0964 | 28.74 | 52.69 | 1.84 | 7.4
27 | 2661 | 144.6192 | 76.875 | 20.799 | 29.6 | 521.592 |  | 5.0964 | 28.64 | 52.93 | 1.59 | 7.5
28 | 2700 | 144.6192 | 76.875 | 21.9545 | 32.76 | 514.176 |  | 5.2159 | 30.36 | 52.21 | 1.21 | 7.4
29 | 2339 | 112.8204 | 61.5 | 16.177 | 31.41 | 435.072 |  | 4.7779 | 28.88 | 52.67 | 1.56 | 7.5
30 | -29615137 | 136.3428 | 87.125 | 17.3325 | 33.44 | 437.544 |  | 3.902 | 29.83 | 53.41 | 1.92 | 7.4
31 | 29617379 | 0 | 0 | 0 |  | 0 |  | 0
TOT | 80147 | 4324.056 | 3228.75 | 571.0481 | 956.38 | 15534.048 | 0 | 163.0465 | 813.3 | 1497.37 | 53.01 | 224.8
AVG | 2585.3871 | 139.4857 | 104.1532 | 18.4209 | 31.8793 | 501.0983 | #DIV/0! | 5.2596 |  | 1453.56 | 51.49 | 217.3

## filtr turb
2023-04-01
COMBINED FILTER TURBIDITY
Date | Filter | Filter | Filter | Filter | Filter | Filter | Average
| Turbidity | Turbidity | Turbidity | Turbidity | Turbidity | Turbidity | Daily
| 12:00 A.M. | 4:00 A.M. | 8:00 A.M. | 12:00 P.M. | 4:00 P.M. | 8:00 P.M. | Turbidity
1 | 0.027 | 0.027 | 0.024 | 0.02 | 0.024 | 0.024 | 0.024333
2 | 0.025 | 0.029 | 0.024 | 0.022 | 0.021 | 0.02 | 0.0235
3 | 0.018 | 0.017 | 0.022 | 0.024 | 0.022 | 0.018 | 0.020167
4 | 0.02 | 0.021 | 0.024 | 0.023 | 0.026 | 0.022 | 0.022667
5 | 0.023 | 0.02 | 0.023 | 0.028 | 0.022 | 0.022 | 0.023
6 | 0.022 | 0.021 | 0.019 | 0.018 | 0.02 | 0.02 | 0.02
7 | 0.02 | 0.019 | 0.033 | 0.037 | 0.019 | 0.021 | 0.024833
8 | 0.02 | 0.021 | 0.019 | 0.027 | 0.026 | 0.026 | 0.023167
9 | 0.026 | 0.022 | 0.03 | 0.022 | 0.022 | 0.02 | 0.023667
10 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.02 | 0.021833
11 | 0.021 | 0.022 | 0.024 |  | 0.029 | 0.027 | 0.0246
12 | 0.024 | 0.024 | 0.026 | 0.023 | 0.024 | 0.022 | 0.023833
13 | 0.024 | 0.022 | 0.027 | 0.025 | 0.026 | 0.02 | 0.024
14 | 0.02 | 0.024 | 0.025 | 0.021 | 0.025 | 0.019 | 0.022333
15 | 0.021 | 0.019 | 0.023 | 0.026 | 0.024 | 0.023 | 0.022667
16 | 0.022 | 0.023 | 0.026 | 0.023 | 0.024 | 0.021 | 0.023167
17 | 0.023 | 0.024 | 0.023 | 0.025 | 0.028 | 0.021 | 0.024
18 | 0.025 | 0.024 | 0.026 | 0.024 | 0.021 | 0.021 | 0.0235
19 | 0.03 | 0.021 | 0.023 | 0.02 | 0.025 | 0.023 | 0.023667
20 | 0.025 | 0.024 | 0.025 | 0.019 | 0.021 | 0.023 | 0.022833
21 | 0.022 | 0.022 | 0.025 | 0.026 | 0.021 | 0.022 | 0.023
22 | 0.021 | 0.021 | 0.025 | 0.022 | 0.02 | 0.023 | 0.022
23 | 0.022 | 0.023 | 0.029 | 0.029 | 0.026 | 0.025 | 0.025667
24 | 0.026 | 0.027 | 0.031 | 0.025 | 0.026 | 0.024 | 0.0265
25 | 0.03 | 0.025 | 0.022 | 0.025 | 0.026 | 0.026 | 0.025667
26 | 0.027 | 0.02 | 0.025 | 0.026 | 0.022 | 0.022 | 0.023667
27 | 0.03 | 0.024 | 0.024 | 0.023 | 0.027 | 0.027 | 0.025833
28 | 0.027 | 0.025 | 0.027 | 0.026 | 0.029 | 0.029 | 0.027167
29 | 0.029 | 0.029 | 0.027 | 0.029 | 0.027 | 0.029 | 0.028333
30 | 0.03 | 0.029 | 0.035 | 0.032 | 0.029 | 0.033 | 0.031333
31 | [6 empty] | #DIV/0!
All results are in NTU's
[6 empty] | MIN. | #DIV/0!
[6 empty] | MAX. | #DIV/0!
[6 empty] | AVG. | #DIV/0!

## entryturb
2023-04-01
ENTRY POINT TURBIDITY
Date | Entry Pt. | Entry Pt. | Entry Pt. | Entry Pt. | Entry Pt. | Entry Pt. | AVERAGE
| Turbidity | Turbidity | Turbidity | Turbidity | Turbidity | Turbidity | DAILY
| 12:00 A.M. | 4:00 A.M. | 8:00 A.M. | 12:00 P.M. | 4:00 P.M. | 8:00 P.M. | TURBIDITY
1 | 0.034 | 0.028 | 0.027 | 0.028 | 0.029 | 0.032 | 0.029667
2 | 0.028 | 0.029 | 0.027 | 0.027 | 0.026 | 0.021 | 0.026333
3 | 0.021 | 0.022 | 0.024 | 0.029 | 0.03 | 0.021 | 0.0245
4 | 0.026 | 0.024 | 0.033 | 0.031 | 0.029 | 0.024 | 0.027833
5 | 0.03 | 0.031 | 0.04 | 0.037 | 0.02 | 0.021 | 0.029833
6 | 0.025 | 0.026 | 0.038 | 0.035 | 0.032 | 0.019 | 0.029167
7 | 0.023 | 0.023 | 0.056 | 0.039 | 0.029 | 0.026 | 0.032667
8 | 0.024 | 0.025 | 0.029 | 0.031 | 0.031 | 0.026 | 0.027667
9 | 0.026 | 0.025 | 0.027 | 0.022 | 0.025 | 0.026 | 0.025167
10 | 0.03 | 0.026 | 0.031 | 0.026 | 0.031 | 0.026 | 0.028333
11 | 0.024 | 0.023 | 0.029 |  | 0.035 | 0.026 | 0.0274
12 | 0.029 | 0.025 | 0.028 | 0.03 | 0.029 | 0.021 | 0.027
13 | 0.024 | 0.024 | 0.03 | 0.026 | 0.034 | 0.022 | 0.026667
14 | 0.02 | 0.028 | 0.035 | 0.024 | 0.029 | 0.026 | 0.027
15 | 0.028 | 0.027 | 0.04 | 0.034 | 0.035 | 0.03 | 0.032333
16 | 0.029 | 0.03 | 0.029 | 0.029 | 0.025 | 0.028 | 0.028333
17 | 0.022 | 0.024 | 0.031 | 0.029 | 0.022 | 0.03 | 0.026333
18 | 0.025 | 0.025 | 0.032 | 0.031 | 0.029 | 0.022 | 0.027333
19 | 0.042 | 0.023 | 0.035 | 0.026 | 0.026 | 0.029 | 0.030167
20 | 0.03 | 0.029 | 0.027 | 0.029 | 0.027 | 0.027 | 0.028167
21 | 0.028 | 0.029 | 0.029 | 0.044 | 0.029 | 0.028 | 0.031167
22 | 0.028 | 0.027 | 0.029 | 0.029 | 0.026 | 0.026 | 0.0275
23 | 0.027 | 0.029 | 0.03 | 0.028 | 0.029 | 0.026 | 0.028167
24 | 0.027 | 0.025 | 0.028 | 0.027 | 0.031 | 0.025 | 0.027167
25 | 0.035 | 0.028 | 0.027 | 0.023 | 0.025 | 0.022 | 0.026667
26 | 0.026 | 0.022 | 0.026 | 0.025 | 0.027 | 0.021 | 0.0245
27 | 0.029 | 0.029 | 0.028 | 0.029 | 0.029 | 0.031 | 0.029167
28 | 0.03 | 0.029 | 0.03 | 0.034 | 0.035 | 0.036 | 0.032333
29 | 0.035 | 0.032 | 0.03 | 0.03 | 0.031 | 0.032 | 0.031667
30 | 0.033 | 0.034 | 0.028 | 0.041 | 0.026 | 0.027 | 0.0315
31 | [6 empty] | #DIV/0!
All results are in NTU's
[6 empty] | MIN. | #DIV/0!
[6 empty] | MAX. | #DIV/0!
[6 empty] | AVG. | #DIV/0!

## cl2 res
2023-04-01
CHLORINE RESIDUAL
Date | Free | Free | Free | Free | Free | Free
| Chlorine | Chlorine | Chlorine | Chlorine | Chlorine | Chlorine | Average
| Residual | Residual | Residual | Residual | Residual | Residual | Daily
| 12:00 A.M. | 4:00 A.M. | 8:00 A.M. | 12:00 P.M. | 4:00 P.M. | 8:00 P.M. | Residual
1 | 1.26 | 1.24 | 1.28 | 1.22 | 1.28 | 1.27 | 1.2583
2 | 1.29 | 1.2 | 1.21 | 1.19 | 1.18 | 1.15 | 1.2033
3 | 1.24 | 1.25 | 1.27 | 1.24 | 1.24 | 1.27 | 1.2517
4 | 1.26 | 1.26 | 1.22 | 1.3 | 1.29 | 1.26 | 1.265
5 | 1.31 | 1.24 | 1.25 | 1.25 | 1.16 | 1.25 | 1.2433
6 | 1.19 | 1.18 | 1.29 | 1.34 | 1.27 | 1.25 | 1.2533
7 | 1.22 | 1.25 | 1.04 | 1.22 | 1.25 | 1.22 | 1.2
8 | 1.2 | 1.22 | 1.24 | 1.31 | 1.24 | 1.25 | 1.2433
9 | 1.24 | 1.21 | 1.29 | 1.29 | 1.29 | 1.26 | 1.2633
10 | 1.3 | 1.24 | 1.25 | 1.23 | 1.34 | 1.33 | 1.2817
11 | 1.24 | 1.15 | 1.23 |  | 1.23 | 1.22 | 1.214
12 | 1.2 | 1.22 | 1.23 | 1.21 | 1.26 | 1.2 | 1.22
13 | 1.3 | 1.27 | 1.32 | 1.3 | 1.18 | 1.19 | 1.26
14 | 1.17 | 1.19 | 1.33 | 1.35 | 1.32 | 1.35 | 1.285
15 | 1.34 | 1.21 | 1.23 | 1.18 | 1.27 | 1.23 | 1.2433
16 | 1.25 | 1.22 | 1.3 | 1.3 | 1.24 | 1.2 | 1.2517
17 | 1.23 | 1.24 | 1.23 | 1.41 | 1.33 | 1.24 | 1.28
18 | 1.31 | 1.19 | 1.19 | 1.37 | 1.39 | 1.33 | 1.2967
19 | 1.28 | 1.24 | 1.22 | 1.37 | 1.22 | 1.23 | 1.26
20 | 1.25 | 1.27 | 1.34 | 1.36 | 1.34 | 1.17 | 1.2883
21 | 1.16 | 1.17 | 1.23 | 1.18 | 1.23 | 1.25 | 1.2033
22 | 1.28 | 1.26 | 1.24 | 1.22 | 1.22 | 1.2 | 1.2367
23 | 1.19 | 1.15 | 1.3 | 1.3 | 1.29 | 1.33 | 1.26
24 | 1.33 | 1.27 | 1.25 | 1.32 | 1.28 | 1.2 | 1.275
25 | 1.23 | 1.14 | 1.03 | 1.05 | 1.25 | 1.2 | 1.15
26 | 1.27 | 1.29 | 1.26 | 1.34 | 1.31 | 1.33 | 1.3
27 | 1.17 | 1.2 | 1.15 | 1.19 | 1.16 | 1.09 | 1.16
28 | 1.25 | 1.28 | 1.31 | 1.31 | 1.07 | 1.13 | 1.225
29 | 1.2 | 1.21 | 1.22 | 1.16 | 1.16 | 1.15 | 1.1833
30 | 1.17 | 1.15 | 1.29 | 1.23 | 1.34 | 1.24 | 1.2367
31
All results are in mg/l
[6 empty] | MIN. | 1.15
[6 empty] | MAX. | 1.3
[6 empty] | AVG. | 1.2431

## ozone
2023-04-01
Ozone Residual
Date | Ozone | Ozone | Ozone | Ozone | Ozone | Ozone | Average
| Residual | Residual | Residual | Residual | Residual | Residual | Daily
| 12:00 A.M. | 04:00 A.M. | 08:00 A.M. | 12:00 P.M. | 4:00 P.M. | 8:00 P.M. | Residual
1 | 0.5 | 0.48 | 0.5 | 0.51 | 0.52 | 0.44 | 0.49167
2 | 0.39 | 0.41 | 0.45 | 0.42 | 0.43 | 0.49 | 0.43167
3 | 0.39 | 0.46 | 0.52 | 0.49 | 0.5 | 0.37 | 0.455
4 | 0.48 | 0.49 | 0.45 | 0.49 | 0.39 | 0.49 | 0.465
5 | 0.46 | 0.44 | 0.47 | 0.43 | 0.42 | 0.45 | 0.445
6 | 0.46 | 0.45 | 0.43 | 0.44 | 0.44 | 0.45 | 0.445
7 | 0.44 | 0.41 | 0.44 | 0.45 | 0.39 | 0.48 | 0.435
8 | 0.5 | 0.46 | 0.52 | 0.47 | 0.43 | 0.43 | 0.46833
9 | 0.45 | 0.47 | 0.44 | 0.45 | 0.45 | 0.46 | 0.45333
10 | 0.39 | 0.5 | 0.46 | 0.48 | 0.41 | 0.46 | 0.45
11 | 0.46 | 0.44 | 0.39 |  | 0.53 | 0.52 | 0.468
12 | 0.56 | 0.54 | 0.41 | 0.44 | 0.45 | 0.46 | 0.47667
13 | 0.47 | 0.48 | 0.47 | 0.48 | 0.57 | 0.48 | 0.49167
14 | 0.46 | 0.49 | 0.39 | 0.5 | 0.47 | 0.42 | 0.455
15 | 0.49 | 0.57 | 0.56 | 0.56 | 0.49 | 0.52 | 0.53167
16 | 0.5 | 0.51 | 0.46 | 0.5 | 0.48 | 0.51 | 0.49333
17 | 0.52 | 0.52 | 0.44 | 0.39 | 0.4 | 0.46 | 0.455
18 | 0.44 | 0.5 | 0.44 | 0.41 | 0.45 | 0.46 | 0.45
19 | 0.46 | 0.49 | 0.44 | 0.45 | 0.44 | 0.4 | 0.44667
20 | 0.45 | 0.49 | 0.5 | 0.49 | 0.49 | 0.48 | 0.48333
21 | 0.45 | 0.47 | 0.44 | 0.4 | 0.43 | 0.46 | 0.44167
22 | 0.44 | 0.45 | 0.37 | 0.51 | 0.42 | 0.49 | 0.44667
23 | 0.46 | 0.47 | 0.52 | 0.56 | 0.48 | 0.48 | 0.495
24 | 0.5 | 0.5 | 0.47 | 0.53 | 0.46 | 0.39 | 0.475
25 | 0.39 | 0.47 | 0.45 | 0.42 | 0.63 | 0.48 | 0.47333
26 | 0.5 | 0.51 | 0.44 | 0.45 | 0.48 | 0.47 | 0.475
27 | 0.44 | 0.5 | 0.46 | 0.47 | 0.46 | 0.39 | 0.45333
28 | 0.46 | 0.45 | 0.46 | 0.44 | 0.49 | 0.45 | 0.45833
29 | 0.47 | 0.48 | 0.42 | 0.46 | 0.5 | 0.47 | 0.46667
30 | 0.44 | 0.45 | 0.44 | 0.48 | 0.5 | 0.48 | 0.465
31
All results are in mg/l
[6 empty] | MIN. | 0.43167
[6 empty] | MAX. | 0.53167
[6 empty] | AVG. | 0.46471

## Fluoride
2023-04-01
FLUORIDE RESIDUAL
Date | Fluoride | Fluoride | Fluoride | Fluoride | Fluoride | Fluoride | Average
| Residual | Residual | Residual | Residual | Residual | Residual | Daily
| 12:00 A.M. | 04:00 A.M. | 08:00 A.M. | 12:00 P.M. | 4:00 P.M. | 8:00 P.M. | Residual
1 | 0.76 | 0.71 | 0.68 | 0.67 | 0.71 | 0.76 | 0.715
2 | 0.74 | 0.62 | 0.69 | 0.67 | 0.69 | 0.75 | 0.69333
3 | 0.67 | 0.69 | 0.72 | 0.76 | 0.67 | 0.74 | 0.70833
4 | 0.71 | 0.71 | 0.66 | 0.73 | 0.73 | 0.7 | 0.70667
5 | 0.68 | 0.73 | 0.76 | 0.77 | 0.7 | 0.74 | 0.73
6 | 0.71 | 0.69 | 0.76 | 0.73 | 0.8 | 0.74 | 0.73833
7 | 0.73 | 0.69 | 0.7 | 0.68 | 0.74 | 0.73 | 0.71167
8 | 0.72 | 0.73 | 0.77 | 0.8 | 0.7 | 0.74 | 0.74333
9 | 0.71 | 0.73 | 0.8 | 0.69 | 0.78 | 0.76 | 0.745
10 | 0.77 | 0.72 | 0.76 | 0.71 | 0.73 | 0.77 | 0.74333
11 | 0.72 | 0.66 | 0.76 |  | 0.8 | 0.73 | 0.734
12 | 0.8 | 0.74 | 0.77 | 0.76 | 0.75 | 0.76 | 0.76333
13 | 0.79 | 0.76 | 0.79 | 0.76 | 0.81 | 0.75 | 0.77667
14 | 0.77 | 0.79 | 0.79 | 0.79 | 0.8 | 0.79 | 0.78833
15 | 0.79 | 0.73 | 0.77 | 0.63 | 0.78 | 0.76 | 0.74333
16 | 0.74 | 0.75 | 0.76 | 0.8 | 0.71 | 0.71 | 0.745
17 | 0.67 | 0.7 | 0.74 | 0.73 | 0.76 | 0.75 | 0.725
18 | 0.7 | 0.69 | 0.77 | 0.74 | 0.77 | 0.7 | 0.72833
19 | 0.71 | 0.74 | 0.75 | 0.73 | 0.75 | 0.72 | 0.73333
20 | 0.71 | 0.74 | 0.81 | 0.84 | 0.71 | 0.73 | 0.75667
21 | 0.71 | 0.75 | 0.78 | 0.77 | 0.8 | 0.74 | 0.75833
22 | 0.72 | 0.76 | 0.75 | 0.8 | 0.77 | 0.77 | 0.76167
23 | 0.76 | 0.79 | 0.77 | 0.8 | 0.74 | 0.79 | 0.775
24 | 0.78 | 0.79 | 0.8 | 0.83 | 0.79 | 0.81 | 0.8
25 | 0.74 | 0.78 | 0.61 | 0.08 | 0.65 | 0.73 | 0.59833
26 | 0.79 | 0.75 | 0.8 | 0.77 | 0.78 | 0.75 | 0.77333
27 | 0.77 | 0.76 | 0.76 | 0.78 | 0.75 | 0.78 | 0.76667
28 | 0.73 | 0.76 | 0.73 | 0.69 | 0.79 | 0.67 | 0.72833
29 | 0.66 | 0.69 | 0.7 | 0.67 | 0.63 | 0.62 | 0.66167
30 | 0.67 | 0.68 | 0.79 | 0.77 | 0.78 | 0.69 | 0.73
31
All results are in mg/l
[6 empty] | MIN. | 0.59833
[6 empty] | MAX. | 0.8
[6 empty] | AVG. | 0.73608

## o3srvc
| Service Water |  | 2023-04-01 |  |  | Cooling Water |  |  | service wtr
Date | HIGH | HIGH | LOW | LOW | TOTAL |  |  |  | minus
| Reading 12AM | Flow | Reading 12AM | Flow | FLOW | Reading 12AM |  | Date | cooling wtr
1 | 18758490 | 0 | 6894215 | 0.015596 | 0.015596 | 50659340 | 2.8208 | 1 | -2.8052
2 | 18758490 | 0 | 6896300 | 0.015618 | 0.015618 | 51036454 | 2.718 | 2 | -2.7024
3 | 18758490 | 0.0002992 | 6898388 | 0.016067 | 0.016366 | 51399823 | 2.7395 | 3 | -2.7231
4 | 18758530 | 0 | 6900536 | 0.015753 | 0.015753 | 51766062 | 2.7091 | 4 | -2.6933
5 | 18758530 | 0 | 6902642 | 0.015858 | 0.015858 | 52128240 | 2.7623 | 5 | -2.7464
6 | 18758530 | 0.0002992 | 6904762 | 0.016314 | 0.016613 | 52497530 | 2.7677 | 6 | -2.7511
7 | 18758570 | 7.48e-05 | 6906943 | 0.01579 | 0.015865 | 52867550 | 2.6728 | 7 | -2.6569
8 | 18758580 | 0 | 6909054 | 0.015633 | 0.015633 | 53224870 | 2.5997 | 8 | -2.5841
9 | 18758580 | 0.0001496 | 6911144 | 0.015753 | 0.015902 | 53572425 | 2.5587 | 9 | -2.5428
10 | 18758600 | 7.48e-05 | 6913250 | 0.015843 | 0.015917 | 53914498 | 2.6171 | 10 | -2.6012
11 | 18758610 | 0.0001496 | 6915368 | 0.01585 | 0.016 | 54264375 | 2.7078 | 11 | -2.6918
12 | 18758630 | 0 | 6917487 | 0.015828 | 0.015828 | 54626385 | 2.7252 | 12 | -2.7094
13 | 18758630 | 0 | 6919603 | 0.015895 | 0.015895 | 54990716 | 2.7102 | 14 | -2.6943
14 | 18758630 | 0 | 6921728 | 0.015671 | 0.015671 | 55353040 | 2.6698 | 14 | -2.6542
15 | 18758630 | 0.0001496 | 6923823 | 0.016142 | 0.016291 | 55709970 | 2.6569 | 15 | -2.6406
16 | 18758650 | 0 | 6925981 | 0.015581 | 0.015581 | 56065170 | 2.6261 | 16 | -2.6106
17 | 18758650 | 0 | 6928064 | 0.015745 | 0.015745 | 56416258 | 2.6566 | 17 | -2.6409
18 | 18758650 | 7.48e-05 | 6930169 | 0.01591 | 0.015985 | 56771420 | 2.5974 | 18 | -2.5814
19 | 18758660 | 7.48e-05 | 6932296 | 0.016157 | 0.016232 | 57118660 | 2.565 | 19 | -2.5487
20 | 18758670 | 0.0001496 | 6934456 | 0.016037 | 0.016187 | 57461570 | 2.6132 | 20 | -2.597
21 | 18758690 | 7.48e-05 | 6936600 | 0.016015 | 0.016089 | 57810925 | 2.6466 | 21 | -2.6305
22 | 18758700 | 0 | 6938741 | 0.015573 | 0.015573 | 58164750 | 2.7593 | 22 | -2.7437
23 | 18758700 | 0 | 6940823 | 0.015708 | 0.015708 | 58533640 | 2.8645 | 23 | -2.8488
24 | 18758700 | 7.48e-05 | 6942923 | 0.015865 | 0.01594 | 58916593 | 2.7448 | 24 | -2.7288
25 | 18758710 | 7.48e-05 | 6945044 | 0.015902 | 0.015977 | 59283543 | 2.7171 | 25 | -2.7011
26 | 18758720 | 7.48e-05 | 6947170 | 0.015783 | 0.015858 | 59646789 | 2.7697 | 26 | -2.7538
27 | 18758730 | 7.48e-05 | 6949280 | 0.01606 | 0.016134 | 60017066 | 2.7581 | 27 | -2.742
28 | 18758740 | 0 | 6951427 | 0.015753 | 0.015753 | 60385799 | 2.7642 | 28 | -2.7484
29 | 18758740 | 0.0001496 | 6953533 | 0.015992 | 0.016142 | 60755340 | 2.6661 | 29 | -2.65
30 | 18758760 | -140.3155 | 6955671 | -52.0284 | -192.3439 | 61111770 | -457.116 | 30 | 264.7721
31 |  | 140.3155 |  | 52.0441 | 192.3596 |  | 459.8067 | 31 | -267.4471
1 | 18758760 |  | 6957765 |  |  | 61471490 |  | 1
SUM |  | 0.0020196 |  | 0.47535 | 0.47737 |  | 80.8749
AVG |  | 6.9641e-05 |  | 0.015851 | 0.015921 |  | 2.6971

## NYC flows
| Catskill |  |  | Croton |  |  | Pump Station
Date | DIGITAL | 2023-04-01 |  |  |  |  | DIGITAL |  |  |  | Average flow | MECHANICAL |  | MECHANICAL
| Reading | Flow |  | Reading 12A | Flow | Flow | Reading | Date | service water | % LOSS |  | Catskill Reading | Flow | Pump Station Reading | Flow | Percent Difference wrt Digital
1 | 29537232 | 2.211 |  |  | 0 | 2.224 | 14301458 | 1 | 0.015596 | 0.1174 | 2.224 | 29340954 | 2.211 | 30359676 | 2.224 | Castsikll Flow | Pump Station Flow | Catskill Reading | Pumpstation Reading
2 | 29539443 | 2.149 |  |  | 0 | 2.191 | 14303682 | 2 | 0.015618 | -1.2276 | 2.191 | 29343165 | 2.149 | 30361900 | 2.19 | 0% | 0.04564% | 0.6645% | -112.3%
3 | 29541592 | 2.17 |  |  | 0 | 2.165 | 14305873 | 3 | 0.016366 | 0.98462 | 2.165 | 29345314 | 2.17 | 30364090 | 2.164 | 0% | 0.04619% | 0.6644% | -112.2%
4 | 29543762 | 2.118 |  |  | 0 | 2.209 | 14308038 | 4 | 0.015753 | -3.5527 | 2.209 | 29347484 | 2.118 | 30366254 | 2.209 | 0% | 0% | 0.6644% | -112.2%
5 | 29545880 | 2.246 |  |  | 0 | 2.229 | 14310247 | 5 | 0.015858 | 1.4629 | 2.229 | 29349602 | 2.246 | 30368463 | 2.229 | 0% | 0% | 0.6643% | -112.2%
6 | 29548126 | 2.196 |  |  | 0 | 2.228 | 14312476 | 6 | 0.016613 | -0.70068 | 2.228 | 29351848 | 2.196 | 30370692 | 2.223 | 0% | 0.2244% | 0.6643% | -112.2%
7 | 29550322 | 2.194 |  |  | 0 | 2.315 | 14314704 | 7 | 0.015865 | -4.7919 | 2.315 | 29354044 | 2.195 | 30372915 | 2.316 | -0.04558% | -0.0432% | 0.6642% | -112.2%
8 | 29552516 | 2.443 |  |  | 0 | 2.458 | 14317019 | 8 | 0.015633 | 0.025919 | 2.458 | 29356239 | 2.442 | 30375231 | 2.457 | 0.04093% | 0.04068% | 0.6642% | -112.2%
9 | 29554959 | 2.438 |  |  | 0 | 2.406 | 14319477 | 9 | 0.015902 | 1.9648 | 2.406 | 29358681 | 2.438 | 30377688 | 2.405 | 0% | 0.04156% | 0.6641% | -112.1%
10 | 29557397 | 2.795 |  |  | 0 | 2.912 | 14321883 | 10 | 0.015917 | -3.6165 | 2.912 | 29361119 | 2.795 | 30380093 | 2.912 | 0% | 0% | 0.6641% | -112.1% | 0
11 | 29560192 | 2.423 |  |  | 0 | 2.395 | 14324795 | 11 | 0.016 | 1.8159 | 2.395 | 29363914 | 2.423 | 30383005 | 2.395 | 0% | 0% | 0.664% | -112.1%
12 | 29562615 | 3.212 |  |  | 0 | 3.329 | 14327190 | 12 | 0.015828 | -3.1498 | 3.329 | 29366337 | 3.212 | 30385400 | 3.329 | 0% | 0% | 0.6639% | -112.1%
13 | 29565827 | 2.995 |  |  | 0 | 3.021 | 14330519 | 13 | 0.015895 | -0.3374 | 3.021 | 29369549 | 2.995 | 30388729 | 3.019 | 0% | 0.0662% | 0.6639% | -112.1%
14 | 29568822 | 3.873 |  |  | 0 | 3.873 | 14333540 | 14 | 0.015671 | 0.40461 | 3.873 | 29372544 | 3.873 | 30391748 | 3.874 | 0% | -0.02582% | 0.6638% | -112%
15 | 29572695 | 2.516 |  |  | 0 | 2.614 | 14337413 | 15 | 0.016291 | -3.2476 | 2.614 | 29376417 | 2.516 | 30395622 | 2.613 | 0% | 0.03826% | 0.6637% | -112%
16 | 29575211 | 2.646 |  |  | 0 | 2.68 | 14340027 | 16 | 0.015581 | -0.69611 | 2.68 | 29378933 | 2.646 | 30398235 | 2.68 | 0% | 0% | 0.6637% | -112%
17 | 29577857 | 3.083 |  |  | 0 | 3.106 | 14342707 | 17 | 0.015745 | -0.23531 | 3.106 | 29381579 | 3.083 | 30400915 | 3.106 | 0% | 0% | 0.6636% | -112%
18 | 29580940 | 2.777 |  |  | 0 | 2.759 | 14345813 | 18 | 0.015985 | 1.2238 | 2.759 | 29384662 | 2.778 | 30404021 | 2.759 | -0.03601% | 0% | 0.6635% | -111.9%
19 | 29583717 | 2.693 |  |  | 0 | 2.82 | 14348572 | 19 | 0.016232 | -4.1132 | 2.82 | 29387440 | 2.694 | 30406780 | 2.82 | -0.03713% | 0% | 0.6635% | -111.9%
20 | 29586410 | 3.27 |  |  | 0 | 3.252 | 14351392 | 20 | 0.016187 | 1.0455 | 3.252 | 29390134 | 3.269 | 30409600 | 3.253 | 0.03058% | -0.03075% | 0.6634% | -111.9%
21 | 29589680 | 3.38 |  |  | 0 | 3.463 | 14354644 | 21 | 0.016089 | -1.9796 | 3.463 | 29393403 | 3.38 | 30412853 | 3.462 | 0% | 0.02888% | 0.6633% | -111.9%
22 | 29593060 | 3.35 |  |  | 0 | 3.481 | 14358107 | 22 | 0.015573 | -3.4456 | 3.481 | 29396783 | 3.35 | 30416315 | 3.481 | 0% | 0% | 0.6633% | -111.8%
23 | 29596410 | 2.146 |  |  | 0 | 2.167 | 14361588 | 23 | 0.015708 | -0.2466 | 2.167 | 29400133 | 2.146 | 30419796 | 2.162 | 0% | 0.2307% | 0.6632% | -111.8%
24 | 29598556 | 3.153 |  |  | 0 | 3.133 | 14363755 | 24 | 0.01594 | 1.1399 | 3.133 | 29402279 | 3.153 | 30421958 | 3.133 | 0% | 0% | 0.6631% | -111.8%
25 | 29601709 | 2.956 |  |  | 0 | 3.056 | 14366888 | 25 | 0.015977 | -2.8424 | 3.056 | 29405432 | 2.7 | 30425091 | 3.056 | 8.66% | 0% | 0.6631% | -111.8%
26 | 29604665 | 2.772 |  |  | 0 | 2.749 | 14369944 | 26 | 0.015858 | 1.4018 | 2.749 | 29408388 | 2.772 | 30428147 | 2.733 | 0% | 0.582% | 0.663% | -111.7%
27 | 29607437 | 2.661 |  |  | 0 | 2.786 | 14372693 | 27 | 0.016134 | -4.0912 | 2.786 | 29411160 | 2.66 | 30430880 | 2.786 | 0.03758% | 0% | 0.6629% | -111.7%
28 | 29610098 | 2.7 |  |  | 0 | 2.747 | 14375479 | 28 | 0.015753 | -1.1573 | 2.747 | 29413820 | 2.702 | 30433666 | 2.747 | -0.07407% | 0% | 0.6629% | -111.7%
29 | 29612798 | 2.339 |  |  | 0 | 2.341 | 14378226 | 29 | 0.016142 | 0.60461 | 2.341 | 29416522 | 2.339 | 30436413 | 2.338 | 0% | 0.1282% | 0.6628% | -111.7%
30 | 29615137 | -29615.137 |  |  | 0 | -14380.567 | 14380567 | 30 | -192.3439 | 52.0913 | -14380.567 | 29418861 | -29418.861 | 30438751 | -30438.751 | 0.6628% | -111.7% | 0.6628% | -111.7%
31 |  | 29617.379 |  |  |  | 14382.935 |  | 31 | 192.3596 | 52.087 | 14382.935 |  | 29421.102 |  | 30441.12 | 0.6627% | -111.6% | #DIV/0! | #DIV/0!
1 | 29617379 | [5 empty] | 14382935 | 1 |  |  |  | 29421102 |  | 30441120 |  |  |  | 0.6627% | -111.6%
SUM |  | 80.147 |  |  |  | 81.477
AVG |  | 2.5854 | #DIV/0! |  |  | 2.6283 |  |  |  |  | 81.477 |  | 79.892 |  | 81.444 | -2990% | -2999%
| sum check | 80.147 |  |  |  | 81.477
| avg check | 2.5854 | #REF! |  |  | 2.6283
Postive Diffrence Value Means the Digital Is Higher Negative Means the Mechanical is Higher

## LAB
LAB RESULTS
2023-04-01 | [18 empty] | DAILY LABORATORY TESTING
RAW WATER | [7 empty] | PUMP STATION | [10 empty] | Date | DISTRIBUTION SAMPLE
DAY | TEMP. oC | pH | TURB. | COLOR | ALK | HARDNSS | F- | TEMP.oC | pH | TURB. | COLOR | ALK | HARD. | F CL2 | T CL2 | F- | PHOS. | Int. | DAY | TEMP | pH | TURB. | COLOR | ALK | HARD. | F CL2 | T CL2 | F- | PHOS. | initials | Location
1 | 13.2 | 7.49 | 1.46 | 7 | 17.5 | 15 | 0.08 | 13.2 | 7.55 | 0.026 | 0 | 20.3 | 17 | 1.22 | 1.28 | 0.75 | 1.77 | PHIL | 1 | 13.9 | 7.71 | 0.029 | 0 | 18 | 16 | 1.09 | 1.18 | 0.66 | 1.5 | MA | BEDFORD
2 | 12.6 | 7.08 | 1.41 | 9 | 14.2 | 16 | 0.06 | 13.9 | 7.51 | 0.032 | 0 | 16.7 | 16 | 1.27 | 1.34 | 0.76 | 1.47 | PHIL | 2 | 17 | 7.73 | 0.079 | 0 | 19.6 | 16 | 0.83 | 0.87 | 0.74 | 1.49 | SL | MT PEAK
3 | 10.3 | 7.24 | 1.51 | 8 | 16.7 | 14 | 0.03 | 11.2 | 7.58 | 0.021 | 0 | 19.8 | 14 | 1.15 | 1.21 | 0.75 | 1.46 | MG | 3 | 15.6 | 7.63 | 0.027 | 0 | 19 | 14 | 1.06 | 1.17 | 0.71 | 1.6 | MA | RED OAK
4 | 9.1 | 6.99 | 1.69 | 10 | 14 | 14 | 0.02 | 11.8 | 7.28 | 0.021 | 0 | 15.8 | 14 | 1.27 | 1.31 | 0.74 | 1.52 | MG | 4 | 18 | 7.68 | 0.039 | 0 | 14.5 | 15 | 1.02 | 1.09 | 0.7 | 1.4 | MA | CAMPFIRE RD
5 | 10.1 | 7.02 | 1.52 | 10 | 15.1 | 14 | 0.07 | 11.7 | 7.47 | 0.024 | 0 | 18.1 | 14 | 1.26 | 1.35 | 0.7 | 1.42 | MG | 5 |  | 8.4 | 0.053 | 0 | 18.6 | 16 | 0.83 | 0.9 | 0.73 | 1.39
6 | 10.3 | 7 | 1.37 | 9 | 16 | 14 | 0.05 | 12.6 | 7.51 | 0.025 | 0 | 20.5 | 16 | 1.24 | 1.36 | 0.71 | 1.58 | SL | 6 | 13.5 | 7.45 | 0.046 | 0 | 18.7 | 15 | 1.36 | 1.36 | 0.71 | 1.45 | TH | SHINGLE HOUSE RD
7 | 12.4 | 6.65 | 1.22 | 7 | 11.4 | 12 | 0.02 | 14.7 | 7.41 | 0.022 | 0 | 18 | 16 | 1.22 | 1.28 | 0.73 | 1.45 | SL | 7 | 13 | 7.2 | 0.029 | 0 | 19.8 | 17 | 1.03 | 1.16 | 0.74 | 1.45 | TH | TOWN HALL
8 | 10.2 | 6.77 | 1.28 | 11 | 12.3 | 14 | 0.04 | 14.3 | 7.46 | 0.024 | 0 | 16.4 | 14 | 1.2 | 1.28 | 0.72 | 1.41 | SL | 8 | 16.6 | 7.6 | 0.028 | 0 | 19 | 16 | 1.03 | 1.08 | 0.74 | 1.44 | PHIL | BEDFORD
9 | 15.8 | 6.99 |  | 8 | 13.8 | 15 | 0.05 | 15 | 7.39 | 0.026 | 0 | 15.7 | 13 | 1.24 | 1.31 | 0.71 | 1.41 | SL | 9 | 15.5 | 7.65 | 0.038 | 0 | 17.4 | 18 | 0.94 | 1.03 | 0.74 | 1.41 | TH | MT PEAK
10 | 10.2 | 7.26 | 1.45 | 8 | 15 | 14 | 0.09 | 11.7 | 7.4 | 0.026 | 0 | 17.6 | 15 | 1.26 | 1.34 | 0.76 | 1.42 | MG | 10 | 12.4 | 7.63 | 0.033 | 0 | 20 | 15 | 1.13 | 1.19 | 0.77 | 1.6 | MA | RED OAK
11 | 9.9 | 6.97 | 1.38 | 9 | 14.2 | 14 | 0.04 | 12.2 | 7.36 | 0.026 | 0 | 17.4 | 14 | 1.33 | 1.37 | 0.77 | 1.45 | MG | 11 | 13.6 | 7.36 | 0.027 | 0 | 17.5 | 13 | 1.08 | 1.19 | 0.8 | 1.69 | MA | CAMPFIRE RD
12 | 10.4 | 7.07 | 1.45 | 9 | 14.5 | 13 | 0.04 | 12.3 | 7.32 | 0.026 | 0 | 16.7 | 14 | 1.22 | 1.28 | 0.73 | 1.39 | MG | 12 | 21.5 | 7.51 | 0.038 | 0 | 15.5 | 15 | 0.92 | 1.03 | 0.76 | 1.47 | TS | DPW
13 | 10.9 | 7.08 | 1.41 | 8 | 13.6 | 13 | 0.06 | 13.5 | 7.44 | 0.021 | 0 | 19.3 | 13 | 1.2 | 1.29 | 0.76 | 1.42 | MG | 13 | 14.4 | 7.52 | 0.029 | 0 | 19 | 16 | 1.21 | 1.28 | 0.8 | 1.42 | TS | SHINGLE HOUSE RD
14 | 13.2 | 7.04 | 1.51 | 9 | 15.6 | 13 | 0.05 | 14.7 | 7.35 | 0.02 | 0 | 14.8 | 14 | 1.17 | 1.25 | 0.77 | 1.41 | SL | 14 | 21 | 7.31 | 0.03 | 0 | 19.914 | 14 | 1.08 | 1.24 | 0.76 | 1.43 |  | TOWN HALL
15 | 12 | 6.64 | 1.51 | 12 | 13.6 | 12 | 0.05 | 13.9 | 7.52 | 0.028 | 0 | 14.1 | 16 | 1.34 | 1.41 | 0.79 | 1.35 | SL | 15 | 16.9 | 7.54 | 0.036 | 0 | 18.5 | 16 | 1.09 | 1.19 | 0.75 | 1.52 | PHIL | BEDFORD
16 | 11.6 | 6.62 | 1.61 | 12 | 13 | 12 | 0.06 | 15.4 | 7.67 | 0.029 | 0 | 14 | 14 | 1.25 | 1.31 | 0.74 | 1.47 | SL | 16 | 19.8 | 7.73 | 0.049 | 0 | 17 | 14 | 0.94 | 1.01 | 0.79 | 1.42 | TH | MT PEAK
17 | 12 | 7.18 | 1.66 | 9 | 14.6 | 13 | 0.01 | 13.7 | 7.51 | 0.028 | 0 | 17.9 | 13 | 1.2 | 1.23 | 0.71 | 1.5 | MG | 17 | 13.4 | 7.93 | 0.029 | 0 | 18.9 | 14 | 0.92 | 1.02 | 0.65 | 1.43 | TH | RED OAK
18 | 11.6 | 6.93 | 1.56 | 7 | 14 | 13 | 0.02 | 12.8 | 7.34 | 0.03 | 0 | 16.7 | 14 | 1.24 | 1.37 | 0.75 | 1.63 | MG | 18 | 13.6 | 7.63 | 0.047 | 0 | 14 | 14 | 1.08 | 1.17 | 0.74 | 1.8 | TH/TS | CAMPFIRE RD
19 | 11.9 | 7.13 | 1.8 | 8 | 11.9 | 12 | 0.04 | 12.4 | 7.5 | 0.022 | 0 | 14.6 | 12 | 1.33 | 1.4 | 0.7 | 1.64 | MG | 19 | 16.3 | 8.09 | 0.042 | 1 | 8 | 12 | 0.89 | 1.01 | 0.74 | 1.44 | PHIL/TS | DPW
20 | 13.9 | 7.2 | 1.62 | 13 | 13.6 | 12 | 0.04 | 14.8 | 7.57 | 0.03 | 0 | 16.6 | 14 | 1.25 | 1.35 | 0.71 | 1.4 | SL | 20 | 16.8 | 7.69 | 0.023 | 0 | 15.5 | 11 | 1.3 | 1.44 | 0.75 | 1.4 | TS | SHINGLE HOUSE RD
21 | 16 | 7.25 | 1.94 | 12 | 13.2 | 12 | 0.04 | 15.7 | 7.53 | 0.028 | 0 | 15.2 | 14 | 1.16 | 1.25 | 0.71 | 1.38 | SL | 21 |  | 7.74 | 0.031 |  | 15.1 | 13 | 0.94 | 1.08 | 0.79 | 1.38 | TS | TOWN HALL
22 | 15.1 | 7.24 | 1.81 | 12 | 12.6 | 12 | 0.07 | 14.5 | 7.45 | 0.028 | 0 | 15.3 | 10 | 1.28 | 1.34 | 0.72 | 1.42 | SL | 22 | 18.5 | 7.68 | 0.03 | 0 | 16.8 | 16 | 1.07 | 1.19 | 0.73 | 1.45 | PHIL | BEDFORD
23 | 12.9 | 7.22 | 1.79 | 12 | 13 | 12 | 0.03 | 16.3 | 7.59 | 0.027 | 0 | 15 | 10 | 1.19 | 1.27 | 0.76 | 1.38 | SL | 23 | 19.7 | 7.62 | 0.04 | 0 | 16.6 | 15 | 0.89 | 0.99 | 0.77 | 1.4 | TH | MT PEAK
24 | 12.6 | 7.18 | 1.85 | 12 | 14 | 14 | 0 | 13.9 | 7.44 | 0.026 | 0 | 15 | 13 | 1.33 | 1.38 | 0.79 | 1.42 | MG | 24 | 17.8 | 8.07 | 0.025 | 0 | 16.8 | 15 | 0.99 | 1.12 | 0.82 | 1.4 | TH/TS | RED OAK
25 | 15 | 7.17 | 1.93 | 13 | 13 | 13 | 0.06 | 16.1 | 7.58 | 0.025 | 0 | 16 | 12 | 1.2 | 1.26 | 0.81 | 1.41 | MG | 25 | 18.9 | 7.6 | 0.028 | 0 | 14 | 12 | 0.87 | 0.95 | 0.69 | 1.4 | TS | CAMPFIRE RD
26 | 12.4 | 7.18 | 1.75 | 12 | 13 | 14 | 0 | 14.6 | 7.45 | 0.022 | 0 | 15 | 13 | 1.2 | 1.26 | 0.73 | 1.38 | MG | 26 | 18.5 | 7.89 | 0.031 | 0 | 16 | 12 | 0.87 | 1 | 0.73 | 1.37 | TS | DPW
27 | 12.7 | 7.3 | 1.58 | 11 | 12.7 | 14 | 0 | 14.5 | 7.55 | 0.021 | 0 | 15.3 | 14 | 1.33 | 1.4 | 0.75 | 1.44 | MG | 27 | 13.5 | 7.61 | 0.027 | 0 | 17.3 | 16 | 1.05 | 1.16 | 0.75 | 1.42 | TS/PHIL | SHINGLE HOUSE RD
28 | 13.1 | 7.28 | 1.1 | 8 | 16.7 | 14 | 0 | 15.5 | 7.45 | 0.029 | 0 | 16.1 | 14 | 1.25 | 1.35 |  | 1.45 | SL | 28 | 14.8 | 7.73 | 0.03 | 0 | 16.8 | 17 | 0.96 | 1.11 | 0.71 | 1.37 | TS/PHIL | TOWN HALL
29 | 15.5 | 7.35 | 1.08 | 8 | 16.3 | 16 | 0 | 17.3 | 7.68 | 0.035 | 0 | 17.4 | 16 | 1.2 | 1.28 | 0.66 | 1.42 | SL | 29 | 18.3 | 7.63 | 0.04 | 0 | 23.3 | 18 | 0.91 | 1.02 | 0.69 | 1.43 | PHIL | BEDFORD
30 | 16.7 | 7.33 | 1.51 | 12 | 15.8 | 14 | 0 | 15.9 | 7.48 | 0.033 | 0 | 18.7 | 14 | 1.17 | 1.25 | 0.67 | 1.44 | SL | 30 | 19.5 | 7.8 | 0.052 | 0 | 18 | 14 | 0.64 | 0.74 | 0.75 | 1.38 | PRS | BEDFORD
31 | [18 empty] | 31

## daf
DAF TURBIDTY | [11 empty] | COMBINE RAW TURB. | % REMOVAL | 2023 DAF TURBIDITY TESTING | [10 empty] | COMBINE RAW TURB. | % REMOVAL
DATE | TIME | #1 | #2 | #3 | #4 | #5 | FLOW | GPM | PSI | COMPUTR | BENCH |  |  | DATE | #1 | #2 | #3 | #4 | #5 | FLOW | GPM | PSI | COMPUTR | BENCH
1 | 1230AM | [5 empty] | 2.56 | 447 | 43 | 0.11 | 0.103 | 1.42 | 92.7465 | 1 | [5 empty] | 2.535 | 447.5 | 42.5 | 0.14 | 0.0975 | 1.42 | 93.1338
1 | 9AM | [5 empty] | 2.51 | 448 | 42 | 0.17 | 0.092 | 1.42 | 93.5211 | 2 | [5 empty] | 2.455 | 449 | 43 | 0.095 | 0.097 | 1.395 | 93.0466
1 | [12 empty] | 93.5211 | 3 | [5 empty] | 2.36 | 445 | 43 | 0.08 | 0.095 | 1.54 | 93.8312
[7 empty] | 2.535 | 447.5 | 42.5 | 0.14 | 0.0975 | 1.42 | 93.1338 | 4 | [5 empty] | 2.54 | 408 | 53 | 0.08 | 0.096 | 1.69 | 94.3195
2 | 1230AM | [5 empty] | 2.46 | 448 | 43 | 0.1 | 0.105 | 1.4 | 92.5 | 5 | [5 empty] | 2.53 | 447.5 | 42.5 | 0.09 | 0.0995 | 1.49 | 93.3221
2 | 2PM | [5 empty] | 2.45 | 450 | 43 | 0.09 | 0.089 | 1.39 | 93.5971 | 6 | [5 empty] | 2.47 | 447.5 | 43 | 0.08 | 0.0815 | 1.39 | 94.1367
2 | [12 empty] | #DIV/0! | 7 | [5 empty] | 2.435 | 447.5 | 43 | 0.065 | 0.0775 | 1.31 | 94.084
[7 empty] | 2.455 | 449 | 43 | 0.095 | 0.097 | 1.395 | 93.0466 | 8 | [5 empty] | 2.765 | 421 | 49.5 | 0.085 | 0.073 | 1.335 | 94.5318
3 | 1225AM | [5 empty] | 2.52 | 445 | 43 | 0.08 | 0.091 | 1.51 | 93.9735 | 9 | [5 empty] | 2.72 | 448.5 | 43 | 0.075 | 0.0875 | 1.38 | 93.6594
3 | 9AM | [5 empty] | 2.2 | 445 | 43 | 0.08 | 0.099 | 1.57 | 93.6943 | 10 | [5 empty] | 2.98 | 440 | 47 | 0.09 | 0.064 | 1.45 | 95.5862
3 | [12 empty] | #DIV/0! | 11 | [5 empty] | 4.1 | 446 | 43 | 0.08 | 0.087 | 1.38 | 93.6957
[7 empty] | 2.36 | 445 | 43 | 0.08 | 0.095 | 1.54 | 93.8312 | 12 | [5 empty] | 3.63 | 449 | 43 | 0.06 | 0.0925 | 1.425 | 93.5088
3.6471 | 1220AM | [5 empty] | 2.54 | 408 | 53 | 0.08 | 0.096 | 1.69 | 94.3195 | 13 | [5 empty] | 3.42 | 447 | 43 | 0.09 | 0.087 | 1.41 | 93.8298
3.8824 | [12 empty] | #DIV/0! | 14 | [5 empty] | 3.235 | 442.5 | 44 | 0.1 | 0.0695 | 1.49 | 95.3356
4.1176 | [12 empty] | #DIV/0! | 15 | [5 empty] | 2.505 | 446 | 43 | 0.07 | 0.0715 | 1.635 | 95.6269
[7 empty] | 2.54 | 408 | 53 | 0.08 | 0.096 | 1.69 | 94.3195 | 16 | [5 empty] | 3.055 | 446.5 | 43 | 0.07 | 0.072 | 1.655 | 95.6495
4.5882 | 12:20AM | [5 empty] | 2.67 | 448 | 42 | 0.09 | 0.102 | 1.52 | 93.2895 | 17 | [5 empty] | 3.305 | 448.5 | 43 | 0.08 | 0.0695 | 1.68 | 95.8631
4.8235 | 1:50PM | [5 empty] | 2.39 | 447 | 43 | 0.09 | 0.097 | 1.46 | 93.3562 | 18 | [5 empty] | 3.63 | 448.5 | 43 | 0.125 | 0.099 | 1.63 | 93.9264
5.0588 | [12 empty] | #DIV/0! | 19 | [5 empty] | 3.025 | 443 | 43.5 | 0.105 | 0.0965 | 1.8 | 94.6389
[7 empty] | 2.53 | 447.5 | 42.5 | 0.09 | 0.0995 | 1.49 | 93.3221 | 20 | [5 empty] | 3.995 | 446 | 43 | 0.115 | 0.087 | 1.92 | 95.4688
5.5294 | 2:00AM | [5 empty] | 2.3 | 448 | 43 | 0.09 | 0.079 | 1.37 | 94.2336 | 21 | [5 empty] | 3.685 | 440.5 | 43.5 | 0.07 | 0.0735 | 1.885 | 96.1008
5.7647 | 5:40PM | [5 empty] | 2.64 | 447 | 43 | 0.07 | 0.084 | 1.41 | 94.0426 | 22 | [5 empty] | 3.835 | 446.5 | 43 | 0.07 | 0.0865 | 1.84 | 95.2989
6 | [12 empty] | #DIV/0! | 23 | [5 empty] | 2.675 | 440.5 | 45 | 0.05 | 0.074 | 1.805 | 95.9003
[7 empty] | 2.47 | 447.5 | 43 | 0.08 | 0.0815 | 1.39 | 94.1367 | 24 | [5 empty] | 2.96 | 426 | 48.5 | 0.035 | 0.0595 | 1.855 | 96.7925
6.7059 | 1:15AM | [5 empty] | 2.39 | 447 | 43 | 0.07 | 0.077 | 1.22 | 93.6885 | 25 | [5 empty] | 3.18 | 445 | 43 | 0.06 | 0.0865 | 1.885 | 95.4111
6.9412 | 9:25PM | [5 empty] | 2.48 | 448 | 43 | 0.06 | 0.078 | 1.4 | 94.4286 | 26 | [5 empty] | 3.23 | 446 | 43 | 0.035 | 0.059 | 1.75 | 96.6286
7.1765 | [12 empty] | #DIV/0! | 27 | [5 empty] | 3.155 | 444.5 | 43 | 0.03 | 0.05 | 1.49 | 96.6443
[7 empty] | 2.435 | 447.5 | 43 | 0.065 | 0.0775 | 1.31 | 94.084 | 28 | [5 empty] | 2.845 | 444.5 | 43 | 0.075 | 0.0675 | 1.13 | 94.0265
7.6471 | 1:00AM | [5 empty] | 2.74 | 394 | 56 | 0.07 | 0.072 | 1.28 | 94.375 | 29 | [5 empty] | 2.72 | 420.5 | 49.5 | 0.095 | 0.077 | 1.07 | 92.8037
7.8824 | 730AM | [5 empty] | 2.79 | 448 | 43 | 0.1 | 0.074 | 1.39 | 94.6763 | 30 | [5 empty] | 2.375 | 448 | 43 | 0.075 | 0.0675 | 1.835 | 96.3215
8.1176 | [12 empty] | #DIV/0! | 31 | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | 2.765 | 421 | 49.5 | 0.085 | 0.073 | 1.335 | 94.5318 | DO NOT PUT NUMBERS IN THIS SPREADSHEET IT CONTAINS FORMULA THAT WILL AVERAGE THE DAF TURBIDITY.
8.5882 | 2AM | [5 empty] | 2.76 | 449 | 43 | 0.07 | 0.081 | 1.35 | 94
8.8235 | 1145AM | [5 empty] | 2.68 | 448 | 43 | 0.08 | 0.094 | 1.41 | 93.3333
9.0588 | [12 empty] | #DIV/0!
[7 empty] | 2.72 | 448.5 | 43 | 0.075 | 0.0875 | 1.38 | 93.6594
9.5294 | 1220AM | [5 empty] | 2.98 | 440 | 47 | 0.09 | 0.064 | 1.45 | 95.5862
9.7647 | [12 empty] | #DIV/0!
10 | [12 empty] | #DIV/0!
[7 empty] | 2.98 | 440 | 47 | 0.09 | 0.064 | 1.45 | 95.5862
10.7059 | 1215AM | [5 empty] | 4.1 | 446 | 43 | 0.08 | 0.087 | 1.38 | 93.6957
10.9412 | [12 empty] | #DIV/0!
11.1765 | [12 empty] | #DIV/0!
[7 empty] | 4.1 | 446 | 43 | 0.08 | 0.087 | 1.38 | 93.6957
11.6471 | 1220AM | [5 empty] | 3.59 | 448 | 43 | 0.03 | 0.086 | 1.45 | 94.069
11.8824 | 530PM | [5 empty] | 3.67 | 450 | 43 | 0.09 | 0.099 | 1.4 | 92.9286
12.1176 | [12 empty] | #DIV/0!
[7 empty] | 3.63 | 449 | 43 | 0.06 | 0.0925 | 1.425 | 93.5088
12.5882 | 12:15AM | [5 empty] | 3.42 | 447 | 43 | 0.09 | 0.087 | 1.41 | 93.8298
12.8235 | [12 empty] | #DIV/0!
13.0588 | [12 empty] | #DIV/0!
[7 empty] | 3.42 | 447 | 43 | 0.09 | 0.087 | 1.41 | 93.8298
13.5294 | 1:10AM | [5 empty] | 2.49 | 440 | 45 | 0.07 | 0.068 | 1.51 | 95.4967
13.7647 | 9:04AM | [5 empty] | 3.98 | 445 | 43 | 0.13 | 0.071 | 1.47 | 95.1701
14 | [12 empty] | #DIV/0!
[7 empty] | 3.235 | 442.5 | 44 | 0.1 | 0.0695 | 1.49 | 95.3356
14.7059 | 2:00AM | [5 empty] | 2.62 | 447 | 43 | 0.07 | 0.079 | 1.51 | 94.7682
14.9412 | 8:30AM | [5 empty] | 2.39 | 445 | 43 | 0.07 | 0.064 | 1.76 | 96.3636
15.1765 | [12 empty] | #DIV/0!
[7 empty] | 2.505 | 446 | 43 | 0.07 | 0.0715 | 1.635 | 95.6269
15.6471 | 1AM | [5 empty] | 3.33 | 447 | 43 | 0.07 | 0.066 | 1.61 | 95.9006
15.8824 | 9AM | [5 empty] | 2.78 | 446 | 43 | 0.07 | 0.078 | 1.7 | 95.4118
16.1176 | [12 empty] | #DIV/0!
[7 empty] | 3.055 | 446.5 | 43 | 0.07 | 0.072 | 1.655 | 95.6495
16.5882 | 1215AM | [5 empty] | 2.8 | 448 | 43 | 0.07 | 0.056 | 1.66 | 96.6265
16.8235 | 415PM | [5 empty] | 3.81 | 449 | 43 | 0.09 | 0.083 | 1.7 | 95.1176
17.0588 | [12 empty] | #DIV/0!
[7 empty] | 3.305 | 448.5 | 43 | 0.08 | 0.0695 | 1.68 | 95.8631
17.5294 | 1220AM | [5 empty] | 3.89 | 448 | 43 | 0.09 | 0.112 | 1.56 | 92.8205
17.7647 | 330PM | [5 empty] | 3.37 | 449 | 43 | 0.16 | 0.086 | 1.7 | 94.9412
18 | [12 empty] | #DIV/0!
[7 empty] | 3.63 | 448.5 | 43 | 0.125 | 0.099 | 1.63 | 93.9264
18.7059 | 1225AM | [5 empty] | 3.21 | 447 | 43 | 0.08 | 0.113 | 1.8 | 93.7222
18.9412 | 1:20PM | [5 empty] | 2.84 | 439 | 44 | 0.13 | 0.08 |  | #DIV/0!
19.1765 | [12 empty] | #DIV/0!
[7 empty] | 3.025 | 443 | 43.5 | 0.105 | 0.0965 | 1.8 | 94.6389
19.6471 | 2:00AM | [5 empty] | 4.09 | 444 | 43 | 0.1 | 0.098 | 1.62 | 93.9506
20.1176 | 11:19AM | [5 empty] | 3.9 | 448 | 43 | 0.13 | 0.076 | 2.22 | 96.5766
20.3529 | [12 empty] | #DIV/0!
[7 empty] | 3.995 | 446 | 43 | 0.115 | 0.087 | 1.92 | 95.4688
20.8235 | 1:30AM | [5 empty] | 3.21 | 437 | 43 | 0.07 | 0.078 | 1.94 | 95.9794
21.0588 | 4:00PM | [5 empty] | 4.16 | 444 | 44 | 0.07 | 0.069 | 1.83 | 96.2295
21.2941 | [12 empty] | #DIV/0!
[7 empty] | 3.685 | 440.5 | 43.5 | 0.07 | 0.0735 | 1.885 | 96.1008
21.7647 | 2:00AM | [5 empty] | 4.2 | 446 | 43 | 0.07 | 0.075 | 1.81 | 95.8564
22 | 10:00AM | [5 empty] | 3.47 | 447 | 43 | 0.07 | 0.098 | 1.87 | 94.7594
22.2353 | [12 empty] | #DIV/0!
[7 empty] | 3.835 | 446.5 | 43 | 0.07 | 0.0865 | 1.84 | 95.2989
23 | 1:00AM | [5 empty] | 2.8 | 448 | 43 | 0.07 | 0.078 | 1.79 | 95.6425
22.9412 | 3PM | [5 empty] | 2.55 | 433 | 47 | 0.03 | 0.07 | 1.82 | 96.1538
23.4118 | [12 empty] | #DIV/0!
[7 empty] | 2.675 | 440.5 | 45 | 0.05 | 0.074 | 1.805 | 95.9003
23.8824 | 1220AM | [5 empty] | 2.87 | 407 | 54 | 0.03 | 0.069 | 1.85 | 96.2703
24.1176 | 11AM | [5 empty] | 3.05 | 445 | 43 | 0.04 | 0.05 | 1.86 | 97.3118
24.3529 | [12 empty] | #DIV/0!
[7 empty] | 2.96 | 426 | 48.5 | 0.035 | 0.0595 | 1.855 | 96.7925
25.0588 | 1225AM | [5 empty] | 4.36 | 445 | 43 | 0.09 | 0.108 | 1.93 | 94.4041
25.2941 | 315PM | [5 empty] | 2 | 445 | 43 | 0.03 | 0.065 | 1.84 | 96.4674
25 | [12 empty] | #DIV/0!
[7 empty] | 3.18 | 445 | 43 | 0.06 | 0.0865 | 1.885 | 95.4111
26 | 1220AM | [5 empty] | 3.03 | 445 | 43 | 0.04 | 0.048 | 1.75 | 97.2571
26.2353 | 3PM | [5 empty] | 3.43 | 447 | 43 | 0.03 | 0.07 |  | #DIV/0!
26 | [12 empty] | #DIV/0!
[7 empty] | 3.23 | 446 | 43 | 0.035 | 0.059 | 1.75 | 96.6286
26.9412 | 12:20AM | [5 empty] | 3.18 | 445 | 43 | 0.03 | 0.047 | 1.58 | 97.0253
27.1765 | 1:30PM | [5 empty] | 3.13 | 444 | 43 | 0.03 | 0.053 | 1.4 | 96.2143
27.4118 | [12 empty] | #DIV/0!
[7 empty] | 3.155 | 444.5 | 43 | 0.03 | 0.05 | 1.49 | 96.6443
27.8824 | 1:30AM | [5 empty] | 2.7 | 445 | 43 | 0.07 | 0.06 | 1.1 | 94.5455
28 | 5:00PM | [5 empty] | 2.99 | 444 | 43 | 0.08 | 0.075 | 1.16 | 93.5345
28.3529 | [12 empty] | #DIV/0!
[7 empty] | 2.845 | 444.5 | 43 | 0.075 | 0.0675 | 1.13 | 94.0265
28.8235 | 1:30AM | [5 empty] | 2.75 | 395 | 56 | 0.08 | 0.071 | 1.08 | 93.4259
29.0588 | 830AM | [5 empty] | 2.69 | 446 | 43 | 0.11 | 0.083 | 1.06 | 92.1698
29.2941 | [12 empty] | #DIV/0!
[7 empty] | 2.72 | 420.5 | 49.5 | 0.095 | 0.077 | 1.07 | 92.8037
30 | 130AM | [5 empty] | 2.32 | 448 | 43 | 0.07 | 0.064 | 1.51 | 95.7616
30 | 830AM | [5 empty] | 2.43 | 448 | 43 | 0.08 | 0.071 | 2.16 | 96.713
30.2353 | [12 empty] | #DIV/0!
[7 empty] | 2.375 | 448 | 43 | 0.075 | 0.0675 | 1.835 | 96.3215
30.7059 | [12 empty] | #DIV/0!
30.9412 | [12 empty] | #DIV/0!
31.1765 | [12 empty] | #DIV/0!
[7 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## KMNO4
| KMNO4 | KMNO4 | KMNO4 | KMNO4 | KMNO4 | KMNO4 |  | Average
Day | Residual | Residual | Residual | Residual | Residual | Residual |  | Daily
| 12:00 A.M. | 04:00 A.M. | 08:00 A.M. | 12:00 P.M. | 4:00 P.M. | 8:00 P.M. |  | Residual
[8 empty] | RM#2 | DAF | EFF
1 | [7 empty] | 0 | 0 | 0
2 | [7 empty] | 0 | 0 | 0
3 | [7 empty] | 0 | 0 | 0
4 | [7 empty] | 0 | 0 | 0
5 | [7 empty] | 0 | 0 | 0
6 | [7 empty] | 0 | 0 | 0
7 | [7 empty] | 0 | 0 | 0
8 | [7 empty] | 0 | 0 | 0
9 | [7 empty] | 0 | 0 | 0
10 | [7 empty] | 0 | 0 | 0
11 | [7 empty] | 0 | 0 | 0
12 | [7 empty] | 0 | 0 | 0
13 | [7 empty] | 0 | 0 | 0
14 | [7 empty] | 0 | 0 | 0
15 | [7 empty] | 0 | 0 | 0
16 | [7 empty] | 0 | 0 | 0
17 | [7 empty] | 0 | 0 | 0
18 | [7 empty] | 0 | 0 | 0
19 | [7 empty] | 0 | 0 | 0
20 | [7 empty] | 0 | 0 | 0
21 | [7 empty] | 0 | 0 | 0
22 | [7 empty] | 0 | 0 | 0
23 | [7 empty] | 0 | 0 | 0
24 | [7 empty] | 0 | 0 | 0
25 | [7 empty] | 0 | 0 | 0
26 | [7 empty] | 0 | 0 | 0
27 | [7 empty] | 0 | 0 | 0
28 | [7 empty] | 0 | 0 | 0
29 | [7 empty] | 0 | 0 | 0
30 | [7 empty] | 0 | 0 | 0
31 | [7 empty] | 0 | 0 | 0
[7 empty] | MIN. | 0 | 0 | 0
All results are in mg/l | [6 empty] | MAX. | 0 | 0 | 0
[7 empty] | AVG. | 0 | 0 | 0

## THCKNER
Thickener Testing | Time | Raw | washwater | supernate | % | w.w.w. tk
|  | NTU | NTU | NTU | removal | level
AVERAGE |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## REP PG1
Public Water System Name: |  |  |  | Reporting Month/Year |  | Date Report Submitted: |  | Source Type(s)
New Castle Consolidated WD |  |  |  | 2022-06-01 |  |  |  | Surface Water [ x ]
|  |  |  | Town, Village or City |  | M M D D Y Y Y Y |  | Groundwater [ ]
Public Water Supply ID |  |  |  | Millwood |  | County |  | GWUDI [ ]
NY 5903442 |  |  |  |  | Valid waiver from disinfection? Yes [ ] No [ X ] | Westchester
Is filtration provided for surface supply? Yes [ x ] No [ ]
Did an emergency occur in any part of the water system? Yes [ ] No [ x ] |  |  |  |  | Wavier #_________________on Date:______________________
Does system have approval to flouridate? Yes [ x ] No [ ]
Millwood Water Treatment Plant
| TREATED | CHLORINATION |  | LIQUID |  |  | CHEMICALS/OTHER TREATMENT
| WATER | GASEOUS |  | HYPO- |  | FREE |  | Finished
Date | VOLUME | CYLINDER | CHLORINE | CHLORITE |  | CHLORINE | Ortho- | Water | See Others
| (1,000 GALs/ | WEIGHT | USE | Gallons |  | RESIDUAL | Phosphate | Fluoride
| DAY) |  | (LBS/DAY) |  |  | (mg/l) | Gallons | (mg/l) | DOH-1015
1 | 2224 |  | 22.54 |  |  | 1.2583 | 6 | 0.715
2 | 2191 |  | 21.68 |  |  | 1.2033 | 6 | 0.69333
3 | 2165 |  | 21.32 |  |  | 1.2517 | 6 | 0.70833
4 | 2209 |  | 21.51 |  |  | 1.265 | 7 | 0.70667
5 | 2229 |  | 21.45 |  |  | 1.2433 | 6 | 0.73
6 | 2228 |  | 21.57 |  |  | 1.2533 | 7 | 0.73833
7 | 2315 |  | 26.4 |  |  | 1.2 | 7 | 0.71167
8 | 2458 |  | 30.72 |  |  | 1.2433 | 7 | 0.74333
9 | 2406 |  | 30.25 |  |  | 1.2633 | 8 | 0.745
10 | 2912 |  | 36.36 |  |  | 1.2817 | 8 | 0.74333
11 | 2395 |  | 28.1 |  |  | 1.214 | 8 | 0.734
12 | 3329 |  | 39.83 |  |  | 1.22 | 10 | 0.76333
13 | 3021 |  | 36.95 |  |  | 1.26 | 9 | 0.77667
14 | 3873 |  | 48.05 |  |  | 1.285 | 11 | 0.78833
15 | 2614 |  | 32.46 |  |  | 1.2433 | 7 | 0.74333
16 | 2680 |  | 34.07 |  |  | 1.2517 | 8 | 0.745
17 | 3106 |  | 39.41 |  |  | 1.28 | 8 | 0.725
18 | 2759 |  | 35.63 |  |  | 1.2967 | 90 | 0.72833
19 | 2820 |  | 35.05 |  |  | 1.26 | 8 | 0.73333
20 | 3252 |  | 41 |  |  | 1.2883 | 8 | 0.75667
21 | 3463 |  | 39.39 |  |  | 1.2033 | 11 | 0.75833
22 | 3481 |  | 38.85 |  |  | 1.2367 | 8 | 0.76167
23 | 2167 |  | 25.57 |  |  | 1.26 | 7 | 0.775
24 | 3133 |  | 34.83 |  |  | 1.275 | 10 | 0.8
25 | 3056 |  | 34.57 |  |  | 1.15 | 7 | 0.59833
26 | 2749 |  | 31.61 |  |  | 1.3 | 7.5 | 0.77333
27 | 2786 |  | 29.6 |  |  | 1.16 | 7.5 | 0.76667
28 | 2747 |  | 32.76 |  |  | 1.225 | 7.5 | 0.72833
29 | 2341 |  | 31.41 |  |  | 1.1833 | 6 | 0.66167
30 | [5 empty] | 1.2367 | 10 | 0.73
31
TOTAL |  |  | 922.94 |  |  | 37.2923 |  | 22.0823
AVERAGE | 2727.8966 |  | 31.8255 |  |  | 1.2431 | 10.55 | 0.73608
Reported by: John Young Title: Chief Operator | [6 empty] | Certification Number: NY 0032778
Signature: Grade Level: 1A | [6 empty] | Date: / /

## REP PG2
Sample | Date of | Sample Type | Total Coliform | E.coli | Free | Raw
Location | Sample | 1. Routine | Positive | Positive | Chlorine | Turbidity
|  | 2. Repeat |  |  | Residual
|  | 3. Hi Turb |  |  | mg/l | NTU
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [ ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [X ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [ ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [ ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [ ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [ ] No
|  |  | [ ] Yes [ ] No | [ ] Yes [ ] No
Sample Collector: _____________________________ Date: _ / / and / / _____________________
Name of Laboratory:Westchester County City:Valhalla Laboratory ELAP Certification #10108
Population Served 16,900 Number of Routine Samples**15 Number of Actual Routine Samples 15
Does and M&AR Violation Exist? [ ] Yes [ X ] No
If YES, check reason(s) below:
___ Two or more positive total coliform samples for systems collecting less than forty (40) or more samples (routine, repeat, or HiTurb) per month.
___ More than 5% positive total coliform samples for system collecting forty (40) or more samples (routine, repeat or Hiturb) per month.
___ When a positive Total Coliform sample is positive for E. Coli and a repeat Total Coliform positive, OR, when a positive Total Coliform
sample is negative for E. Coli, but the repeat Total Coliform sample is positive and also is positive for E. Coli.
**Must collect a minimum of five (5) routine samples during the month following a repeat sample collection.

## REP PG3
©Copyright 1992-95, WindowChem Software, Inc., All Rights Reserved., (707) 864-0845, Revision 3.0
NEW YORK STATE DEPARTMENT OF HEALTH | [20 empty] | Water Systems Operation Report
Bureau of Public Water Supply Protection
SURFACE WATER SYSTEMS
Instructions: Complete form and submit to your local health unit within 10 days of the close of the reporting month.
NAME OF PUBLIC WATER SYSTEM |  |  | PROGRAM CODE |  |  |  | STATION | [8 empty] | REPORTING MONTH/YEAR
New Castle Consolidated WD |  |  |  | 1 | 0 | 0 |  | 5 | 9 | 0 | 3 | 4 | 4 | 2 |  |  | 0 | 5 | 2 | 2
Location | Millwood | [7 empty] | County |  |  | Westchester
(C,V,T)
Did an emergency occur in any part of the water system? | [16 empty] | Yes |  | No | x
Did source water bypass a process or were any of the processes inoperative or not operating | [16 empty] | Yes |  | No | x
as designed to modified to operate?
Were the pressure problems in the distribution system? | [16 empty] | Yes |  | No | x
Indicate name of sources used during the month:
Surface sources (s) |  |  |  | NYCDEP Catskill Aqueduct
Ground source(s)
Sample taken at |  |  |  | Millwood Pumping Station | [9 empty] | entry point to the distribution system.
NAME OF ENTRY POINT
The maximum allowable turbidity limit for the point of entry is | [9 empty] | 0.3 |  | NTUs.
1. Were daily turbidity analyses performed by the nephelometric method? | [13 empty] | Yes | x | No
2. Did a single repeat sample confirm that the maximum allowable turbidity | [15 empty] | DATE |  |  |  |  | No | x
limit has been exceeded? | [13 empty] | Yes
3. Did the turbidity, based on an average (and rounded to the nearest whole | [13 empty] | Yes |  | MCL DATE |  |  |  |  | No | x
number) for two consecutive days, exceed five turbidity?
4. Did the turbidity, as determined by a monthly average ( and rounded to the | [13 empty] | Yes |  | MCL DATE |  |  |  |  | No | x
nearest whole number) exceed the maximum allowable turbidity limit?
COMMENTS and/or REMARKS
Forms by EnviroWin (312-244-1900)
Reported by |  | John M. Young | [13 empty] | Date
Title | Chief Operator |  |  | Signature | [12 empty] | Cert. No. |  |  | NY0032778

## REP PG4
©Copyright 1992-95, WindowChem Software, Inc., All Rights Reserved., (707) 864-0845, Revision 3.0
NEW YORK STATE DEPARMENT OF HEALTH
DAILY OPERATION RECORD for this month of |  |  |  |  | 2022-06-01
Catskill Aqueduct
Distribution Turbidity Results
| Amount of | Amount of | Raw | Chemicals | Post Chlorination | [6 empty] | Finished Water Turbidity |  |  |  | Date |  | Free
| of Raw | of Raw | Water | [11 empty] | Sample Location | Sample | Turbidity | Chlorine
| Water | Water | Turbidity |  | Gaseous |  |  |  |  | Liquid | Free |  |  |  |  | Taken |  | Residual
| (Catskill) | (Croton) |  | Alum | #1 | #2 | #3 | #4 | Chlorine | Hypo- | Chlorine | Finish | Pump | Two |  |  |  | mg/l
DATE | 1,000 Gals. | 1,000 Gals. |  | lbs. per | Weight | Weight | Weight | Weight | used | chlorite | Residual | Water | Station | consec. | BEDFORD | 1 | 0.029 | 1.09
| Per Day | Per Day |  | 24 hrs. | of | of | of | of | lbs. per | used | mg/l | Turbidity. | Turbidity | day | MT PEAK | 2 | 0.079 | 0.83
[5 empty] | cylinders | cylinders | cylinders #2 | cylinders #2 | 24. hrs | qts. |  |  |  | aver. | Mobil | 3 | 0.027 | 1.06
1 | 2211 |  |  |  | 0 | 150 | 150 | 150 | 31 |  | 1.2033 |  | 0.029667 |  | CAMPFIRE RD | 4 | 0.039 | 1.02
2 | 2149 |  |  |  | 0 | 119 | 150 | 150 | 24.2 |  | 1.2517 |  | 0.026333 |  |  | 5 | 0.053 | 0.83
3 | 2170 |  |  |  | 0 | 64.8 | 150 | 150 | 27.8 |  | 1.265 |  | 0.0245 |  | SHINGLE HOUSE RD | 6 | 0.046 | 1.36
4 | 2118 |  |  |  | 0 | 67 | 150 | 150 | 21.8 |  | 1.2433 |  | 0.027833 |  | TOWN HALL | 7 | 0.029 | 1.03
5 | 2246 |  |  |  | 0 | 45.2 | 150 | 150 | 27.8 |  | 1.2433 |  | 0.029833 |  | BEDFORD | 8 | 0.028 | 1.03
6 | 2196 |  |  |  | 0 | 17.4 | 150 | 150 | 17.4 |  | 1.2533 |  | 0.029167 |  | MT PEAK | 9 | 0.038 | 0.94
7 | 2194 |  |  |  | 150 | 150 | 150 | 150 | 31.8 |  | 1.2 |  | 0.032667 |  | RED OAK | 10 | 0.033 | 1.13
8 | 2443 |  |  |  | 150 | 150 | 118.2 | 150 | 28.2 |  | 1.2433 |  | 0.027667 |  | CAMPFIRE RD | 11 | 0.027 | 1.19
9 | 2438 |  |  |  | 150 | 150 | 90 | 150 | 27 |  | 1.2633 |  | 0.025167 |  | DPW | 12 | 0.038 | 0.92
10 | 2795 |  |  |  | 150 | 150 | 63 | 150 | 34 |  | 1.2817 |  | 0.028333 |  | SHINGLE HOUSE RD | 13 | 0.029 | 1.21
11 | 2423 |  |  |  | 150 | 150 | 29 | 150 | 26.6 |  | 1.214 |  | 0.0274 |  | TOWN HALL | 14 | 0.03 | 1.08
12 | 3212 |  |  |  | 150 | 150 | 2.4 | 150 | 48.2 |  | 1.22 |  | 0.027 |  | BEDFORD | 15 | 0.036 | 1.09
13 | 2995 |  |  |  | 150 | 150 | 0 | 104.2 | 34.4 |  | 1.26 |  | 0.026667 |  | MT PEAK | 16 | 0.049 | 0.94
14 | 3873 |  |  |  | 150 | 150 | 0 | 69.8 | 43.6 |  | 1.285 |  | 0.027 |  | RED OAK | 17 | 0.029 | 0.92
15 | 2516 |  |  |  | 150 | 150 | 0 | 26.2 | 30.2 |  | 1.2433 |  | 0.032333 |  | CAMPFIRE RD | 18 | 0.047 | 1.08
16 | 2646 |  |  |  | 150 | 150 | 0 | 0 | 22.6 |  | 1.2517 |  | 0.028333 |  | DPW | 19 | 0.042 | 0.89
17 | 3083 |  |  |  | 127.4 | 150 | 0 | 0 | 35.2 |  | 1.28 |  | 0.026333 |  | SHINGLE HOUSE RD | 20 | 0.023 | 1.3
18 | 2777 |  |  |  | 92.2 | 150 | 0 | 0 | 36 |  | 1.2967 |  | 0.027333 |  | TOWN HALL | 21 | 0.031 | 0.94
19 | 2693 |  |  |  | 56.2 | 150 | 0 | 0 | 36.2 |  | 1.26 |  | 0.030167 |  | BEDFORD | 22 | 0.03 | 1.07
20 | 3270 |  |  |  | 20 | 150 | 0 | 0 | 28.6 |  | 1.2883 |  | 0.028167 |  | MT PEAK | 23 | 0.04 | 0.89
21 | 3380 |  |  |  | 0 | 141.4 | 0 | 0 | 50.8 |  | 1.2033 |  | 0.031167 |  | RED OAK | 24 | 0.025 | 0.99
22 | 3350 |  |  |  | 0 | 90.6 | 150 | 150 | 30.4 |  | 1.2367 |  | 0.0275 |  | CAMPFIRE RD | 25 | 0.028 | 0.87
23 | 2146 |  |  |  | 0 | 60.2 | 150 | 150 | 28.8 |  | 1.26 |  | 0.028167 |  | DPW | 26 | 0.031 | 0.87
24 | 3153 |  |  |  | 0 | 31.4 | 150 | 150 | 44.2 |  | 1.275 |  | 0.027167 |  | SHINGLE HOUSE RD | 27 | 0.027 | 1.05
25 | 2956 |  |  |  | 0 | 0 | 137.2 | 150 | 22.2 |  | 1.15 |  | 0.026667 |  | TOWN HALL | 28 | 0.03 | 0.96
26 | 2772 |  |  |  | 0 | 0 | 115 | 150 | 28.4 |  | 1.3 |  | 0.0245 |  | BEDFORD | 29 | 0.04 | 0.91
27 | 2661 |  |  |  | 0 | 0 | 86.6 | 150 | 28.4 |  | 1.16 |  | 0.029167 |  | BEDFORD | 30 | 0.052 | 0.64
28 | 2700 |  |  |  | 0 | 0 | 58.2 | 150 | 26.2 |  | 1.225 |  | 0.032333 |  |  | 31
29 | 2339 |  |  |  | 150 | 150 | 32 | 150 | 22 |  | 1.1833 |  | 0.031667
30 | -29615137 |  |  |  | 150 | 150 | 10 | 150 | 26.2 |  | 1.2367 |  | 0.0315 |  | AVERAGE |  | 0.035621
31 | 29617379 | [11 empty] | #DIV/0!
1
Total | 80147 |  |  |  | 2095.8 |  |  |  | 920.2
Aver. | 2585.3871 |  |  |  | 69.86 |  |  |  | 30.6733 |  | 1.2426 |  | #DIV/0!
DOH-1015 (1/91) P. 2 OF 2

## O3CT
Millwood Water Treatment Plant
Monthly CT Monitoring Report
Month
Year | 2000
DATA INPUT | [9 empty] | DATA OUTPUT
ALL PARAMETERS REPORTED AT PEAK HOUR FLOW | [9 empty] | DO NOT INPUT DATA IN THIS TABLE
| [a] |  |  |  |  | Stage 1 | Stage 2 | Stage 3
[6 empty] | Ozone | Ozone | Ozone
| Peak Hourly | # of Ozone | Ozone | Ozone | Ozone | Residual | Residual | Residual | Raw | Actual CT Provided (min*mg/L*T10/T)
| Raw Water | Contactors | Applied to | Applied to | Applied to | Leaving | Leaving | Leaving | Water | [b] | [c] [d] | [c] [d] | Required | CT
| Flow | In Service | Stage 1 | Stage 2 | Stage 3 | Contactor | Contactor | Contactor | Temp. | Stage 1 | Stage 2 | Stage 3 | 1 log Giardia | Fraction | Compliance
Date | MGD | (1 or 2) | (Yes or No) | (Yes or No) | (Yes or No) | mg/L | mg/L | mg/L | deg. C | Contactor | Contactor | Contactor | (min*mg/L) | Achieved | Yes/No
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Average
Maximum
Minimum
(a) CT calculation shall be determined for PEAK HOUR RAW WATER FLOW each day.
Thus, the raw water quality data and ozone residual data input into this table shall be from that hour
during the day in which the raw water flowrate was greatest.
[b] If Ozone residual is < or = 0.3 mg/L, no credit is given, if the Ozone residual is > 0.3 mg/L, a 1/2 log credit is earned at the raw water temperature.
This model assumes ozone will always be added to the 1st stage.
[c] If Ozone is applied C = C/2, otherwise C = C
[d] Contactor T10/T = |  | 0.53

## CT1
1 Log Giardia Inactivation for Ozone
Data from the |  | Calculated |  | % Diff
Compliance Manual |  | Required | Temp | from
|  | CT |  | Manual
Y Data | X Data
CT | Temp
Best Fit Equation:
y = 0.9781e^(-0.0723x)
Calculated Required CT Eq.:
y = (0.9781e^(-0.0723x))+0.06
e = 2.718

## FILT 1&2
NEW YORK STATE DEPARTMENT OF HEALTH | [12 empty] | Water Systems Operation Report
Bureau of Public Water Supply Protection
Instructions: Complete form and submit to your local health unit within 10 days of the close of the reporting month. | [12 empty] | FILTERED SURFACE WATER SYSTEMS
continuation sheet
FILTER EFFLUENT TURBIDITY NO. 1 | [6 empty] | FILTER EFFLUENT TURBIDITY NO. 2
DATE | 0 | 400 | 800 | 1200 | 1600 | 2000 | DATE | 0 | 400 | 800 | 1200 | 1600 | 2000
1 | [6 empty] | 1
2 | [6 empty] | 2
3 | [6 empty] | 3
4 | [6 empty] | 4
5 | [6 empty] | 5
6 | [6 empty] | 6
7 | [6 empty] | 7
8 | [6 empty] | 8
9 | [6 empty] | 9
10 | [6 empty] | 10
11 | [6 empty] | 11
12 | [6 empty] | 12
13 | [6 empty] | 13
14 | [6 empty] | 14
15 | [6 empty] | 15
16 | [6 empty] | 16
17 | [6 empty] | 17
18 | [6 empty] | 18
19 | [6 empty] | 19
20 | [6 empty] | 20
21 | [6 empty] | 21
22 | [6 empty] | 22
23 | [6 empty] | 23
24 | [6 empty] | 24
25 | [6 empty] | 25
26 | [6 empty] | 26
27 | [6 empty] | 27
28 | [6 empty] | 28
29 | [6 empty] | 29
30 | [6 empty] | 30
31 | [6 empty] | 31
Total No. Measurements_____________________________ | [6 empty] | Total No. Measurements_____________________________
Total No. above Perf. Std.____________________________ | [6 empty] | Total No. above Perf. Std.____________________________
Any measurements above 5 NTU? If yes, please note on | [6 empty] | Any measurements above 5 NTU? If yes, please note on
|  |  |  | DOH-3634 | [6 empty] | DOH-3634
DOH-3634

## FILT 5&6
FILTER EFFLUENT TURBIDITY |  |  |  | NAME OF PUBLIC |  |  | PROGRAM |  | FEDERAL ID |  |  | REPORTING
MONITORING |  |  |  | WATER SYSTEM |  |  | CODE |  | NUMBER |  |  | MONTH/YEAR
|  |  |  | New Castle Consolidated WD |  |  | 100 |  | 5903442
FILTER EFFLUENT TURBIDITY NO. 5 | [6 empty] | FILTER EFFLUENT TURBIDITY NO. 6
DATE | 0 | 400 | 800 | 1200 | 1600 | 2000 | DATE | 0 | 400 | 800 | 1200 | 1600 | 2000
1 | [6 empty] | 1
2 | [6 empty] | 2
3 | [6 empty] | 3
4 | [6 empty] | 4
5 | [6 empty] | 5
6 | [6 empty] | 6
7 | [6 empty] | 7
8 | [6 empty] | 8
9 | [6 empty] | 9
10 | [6 empty] | 10
11 | [6 empty] | 11
12 | [6 empty] | 12
13 | [6 empty] | 13
14 | [6 empty] | 14
15 | [6 empty] | 15
16 | [6 empty] | 16
17 | [6 empty] | 17
18 | [6 empty] | 18
19 | [6 empty] | 19
20 | [6 empty] | 20
21 | [6 empty] | 21
22 | [6 empty] | 22
23 | [6 empty] | 23
24 | [6 empty] | 24
25 | [6 empty] | 25
26 | [6 empty] | 26
27 | [6 empty] | 27
28 | [6 empty] | 28
29 | [6 empty] | 29
30 | [6 empty] | 30
31 | [6 empty] | 31
Total No. Measurements_____________________________ | [6 empty] | Total No. Measurements_____________________________
Total No. above Perf. Std.____________________________ | [6 empty] | Total No. above Perf. Std.____________________________
Any measurements above 5 NTU? If yes, please note on | [6 empty] | Any measurements above 5 NTU? If yes, please note on
|  |  |  | DOH-3634 | [6 empty] | DOH-3634
DOH-3634

## FILT 3&4
FILTER EFFLUENT TURBIDITY |  |  |  | NAME OF PUBLIC |  |  | PROGRAM |  | FEDERAL ID |  |  | REPORTING
MONITORING |  |  |  | WATER SYSTEM |  |  | CODE |  | NUMBER |  |  | MONTH/YEAR
|  |  |  | New Castle Consolidated WD |  |  | 100 |  | 5903442
FILTER EFFLUENT TURBIDITY NO. 3 | [6 empty] | FILTER EFFLUENT TURBIDITY NO. 4
DATE | 0 | 400 | 800 | 1200 | 1600 | 2000 | DATE | 0 | 400 | 800 | 1200 | 1600 | 2000
1 | [6 empty] | 1
2 | [6 empty] | 2
3 | [6 empty] | 3
4 | [6 empty] | 4
5 | [6 empty] | 5
6 | [6 empty] | 6
7 | [6 empty] | 7
8 | [6 empty] | 8
9 | [6 empty] | 9
10 | [6 empty] | 10
11 | [6 empty] | 11
12 | [6 empty] | 12
13 | [6 empty] | 13
14 | [6 empty] | 14
15 | [6 empty] | 15
16 | [6 empty] | 16
17 | [6 empty] | 17
18 | [6 empty] | 18
19 | [6 empty] | 19
20 | [6 empty] | 20
21 | [6 empty] | 21
22 | [6 empty] | 22
23 | [6 empty] | 23
24 | [6 empty] | 24
25 | [6 empty] | 25
26 | [6 empty] | 26
27 | [6 empty] | 27
28 | [6 empty] | 28
29 | [6 empty] | 29
30 | [6 empty] | 30
31 | [6 empty] | 31
Total No. Measurements_____________________________ | [6 empty] | Total No. Measurements_____________________________
Total No. above Perf. Std.____________________________ | [6 empty] | Total No. above Perf. Std.____________________________
Any measurements above 5 NTU? If yes, please note on | [6 empty] | Any measurements above 5 NTU? If yes, please note on
|  |  |  | DOH-3634 | [6 empty] | DOH-3634
DOH-3634

## T.O.C.
Total Organic Carbons |  |  |  | June 2022
Take sample every Monday
code:2640
units - cm-1
Month: | Raw Water | Floated Water | Filtered | % Removal from D.A.F. | % Removal from filtration | Total % Removal
1st Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2nd Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3rd Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
4th Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
(5th) Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Turbidity-NTU | Raw Water NTU | Floated Water NTU | Filtered | % Removal from D.A.F. | % Removal from filtration | Total % Removal
1st Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2nd Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3rd Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
4th Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
(5th) Week |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!

## CT1-2
1/2 Log Giardia Inactivation for Ozone
Data from the |  | Calculated |  | % Diff
Compliance Manual |  | Required | Temp | from
|  | CT |  | Manual
Y Data | X Data
CT | Temp
Best Fit Equation:
y = 0.4843e^(-0.072x)

## DOH4303-1
New York State Department of Health | [5 empty] | Water System Operation Report
Bureau of Public Water Supply Protection
FILTERED SURFACE WATER SYSTEMS
Instructions: Complete pages 1 and 2 of this form and submit to your local health department within 10 days of the close of the reporting month.
Complete page 3 if your system utilizes conventional or direct filtration and can answer "YES" to any of the four questions on page 3.
Public Water System Name |  |  |  | Reporting Month/Year |  |  | Type of Filtration
New Castle Consolidate WD |  |  |  | 2023-04-01 |  |  | Conventional |  |  | Direct
Public Water System ID # |  |  |  | Town, Village,or City |  | County | Alternative |  |  | Slow Sand
NY | 5903442 |  |  | Millwood |  | Westchester | Diatom Earth
| Entry Point Chlorine Residual (mg/L) | [5 empty] | Distribution System Turbidity Results
Date | 0000 | 0400 | 0800 | 1200 | 1600 | 2000 | Sample Location |  |  |  | (NTU)
1 | 1.26 | 1.24 | 1.28 | 1.22 | 1.28 | 1.27 | BEDFORD |  |  |  | 0.029
2 | 1.29 | 1.2 | 1.21 | 1.19 | 1.18 | 1.15 | MT PEAK |  |  |  | 0.079
3 | 1.24 | 1.25 | 1.27 | 1.24 | 1.24 | 1.27 | RED OAK |  |  |  | 0.027
4 | 1.26 | 1.26 | 1.22 | 1.3 | 1.29 | 1.26 | CAMPFIRE RD |  |  |  | 0.039
5 | 1.31 | 1.24 | 1.25 | 1.25 | 1.16 | 1.25 |  |  |  |  | 0.053
6 | 1.19 | 1.18 | 1.29 | 1.34 | 1.27 | 1.25 | SHINGLE HOUSE RD |  |  |  | 0.046
7 | 1.22 | 1.25 | 1.04 | 1.22 | 1.25 | 1.22 | TOWN HALL |  |  |  | 0.029
8 | 1.2 | 1.22 | 1.24 | 1.31 | 1.24 | 1.25 | BEDFORD |  |  |  | 0.028
9 | 1.24 | 1.21 | 1.29 | 1.29 | 1.29 | 1.26 | MT PEAK |  |  |  | 0.038
10 | 1.3 | 1.24 | 1.25 | 1.23 | 1.34 | 1.33 | RED OAK |  |  |  | 0.033
11 | 1.24 | 1.15 | 1.23 |  | 1.23 | 1.22 | CAMPFIRE RD |  |  |  | 0.027
12 | 1.2 | 1.22 | 1.23 | 1.21 | 1.26 | 1.2 | DPW |  |  |  | 0.038
13 | 1.3 | 1.27 | 1.32 | 1.3 | 1.18 | 1.19 | SHINGLE HOUSE RD |  |  |  | 0.029
14 | 1.17 | 1.19 | 1.33 | 1.35 | 1.32 | 1.35 | TOWN HALL |  |  |  | 0.03
15 | 1.34 | 1.21 | 1.23 | 1.18 | 1.27 | 1.23 | BEDFORD |  |  |  | 0.036
16 | 1.25 | 1.22 | 1.3 | 1.3 | 1.24 | 1.2 | MT PEAK |  |  |  | 0.049
17 | 1.23 | 1.24 | 1.23 | 1.41 | 1.33 | 1.24 | RED OAK |  |  |  | 0.029
18 | 1.31 | 1.19 | 1.19 | 1.37 | 1.39 | 1.33 | CAMPFIRE RD |  |  |  | 0.047
19 | 1.28 | 1.24 | 1.22 | 1.37 | 1.22 | 1.23 | DPW |  |  |  | 0.042
20 | 1.25 | 1.27 | 1.34 | 1.36 | 1.34 | 1.17 | SHINGLE HOUSE RD |  |  |  | 0.023
21 | 1.16 | 1.17 | 1.23 | 1.18 | 1.23 | 1.25 | TOWN HALL |  |  |  | 0.031
22 | 1.28 | 1.26 | 1.24 | 1.22 | 1.22 | 1.2 | BEDFORD |  |  |  | 0.03
23 | 1.19 | 1.15 | 1.3 | 1.3 | 1.29 | 1.33 | MT PEAK |  |  |  | 0.04
24 | 1.33 | 1.27 | 1.25 | 1.32 | 1.28 | 1.2 | RED OAK |  |  |  | 0.025
25 | 1.23 | 1.14 | 1.03 | 1.05 | 1.25 | 1.2 | CAMPFIRE RD |  |  |  | 0.028
26 | 1.27 | 1.29 | 1.26 | 1.34 | 1.31 | 1.33 | DPW |  |  |  | 0.031
27 | 1.17 | 1.2 | 1.15 | 1.19 | 1.16 | 1.09 | SHINGLE HOUSE RD |  |  |  | 0.027
28 | 1.25 | 1.28 | 1.31 | 1.31 | 1.07 | 1.13 | TOWN HALL |  |  |  | 0.03
29 | 1.2 | 1.21 | 1.22 | 1.16 | 1.16 | 1.15 | BEDFORD |  |  |  | 0.04
30 | 1.17 | 1.15 | 1.29 | 1.23 | 1.34 | 1.24 | BEDFORD |  |  |  | 0.052
31
[7 empty] | Monthly Turbidity Average: |  |  |  | 0.035621
Location of Entry Point: |  |  | Pump Station Sink
Population Served: |  |  | 16800
Entry Point Disinfection Monitoring: | [6 empty] | If Grab, number of samples per day: |  |  |  | 6
Monitoring Results:
Did the Entry Point residual fall below 0.2 mg/L for more than 4 hours ? | [6 empty] | ……………………………………………………………………
Did the monthly average of the distribution system turbidity results exceed 5 NTU? ………………………………
Reported by (print name): |  |  | John M. Young |  |  |  |  | Title: | Chief Operator
NYSDOH Operator Certification Number : NY |  |  |  |  | 32778 |  | Operator Grade Level: |  | IA
Signature: | [7 empty] | Date:
DOH-4303 (1/05) Page 1 of 3

## DOH4303-2
Compostite Filter Effluent Monitoring
| Date | Results (NTU)
|  | 0000 | 0400 | 0800 | 1200 | 1600 | 2000
| 1 | 0.027 | 0.027 | 0.024 | 0.02 | 0.024 | 0.024
| 2 | 0.025 | 0.029 | 0.024 | 0.022 | 0.021 | 0.02
| 3 | 0.018 | 0.017 | 0.022 | 0.024 | 0.022 | 0.018
| 4 | 0.02 | 0.021 | 0.024 | 0.023 | 0.026 | 0.022
| 5 | 0.023 | 0.02 | 0.023 | 0.028 | 0.022 | 0.022
| 6 | 0.022 | 0.021 | 0.019 | 0.018 | 0.02 | 0.02
| 7 | 0.02 | 0.019 | 0.033 | 0.037 | 0.019 | 0.021
| 8 | 0.02 | 0.021 | 0.019 | 0.027 | 0.026 | 0.026
| 9 | 0.026 | 0.022 | 0.03 | 0.022 | 0.022 | 0.02
| 10 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.02
| 11 | 0.021 | 0.022 | 0.024 |  | 0.029 | 0.027
| 12 | 0.024 | 0.024 | 0.026 | 0.023 | 0.024 | 0.022
| 13 | 0.024 | 0.022 | 0.027 | 0.025 | 0.026 | 0.02
| 14 | 0.02 | 0.024 | 0.025 | 0.021 | 0.025 | 0.019
| 15 | 0.021 | 0.019 | 0.023 | 0.026 | 0.024 | 0.023
| 16 | 0.022 | 0.023 | 0.026 | 0.024 | 0.021 | 0.021
| 17 | 0.023 | 0.024 | 0.023 | 0.025 | 0.028 | 0.021
| 18 | 0.025 | 0.024 | 0.026 | 0.024 | 0.021 | 0.021
| 19 | 0.025 | 0.025 | 0.032 | 0.031 | 0.029 | 0.022
| 20 | 0.025 | 0.024 | 0.025 | 0.019 | 0.021 | 0.023
| 21 | 0.022 | 0.022 | 0.025 | 0.026 | 0.021 | 0.022
| 22 | 0.021 | 0.021 | 0.025 | 0.022 | 0.02 | 0.023
| 23 | 0.022 | 0.023 | 0.029 | 0.029 | 0.026 | 0.025
| 24 | 0.026 | 0.027 | 0.031 | 0.025 | 0.026 | 0.024
| 25 | 0.03 | 0.025 | 0.022 | 0.025 | 0.026 | 0.026
| 26 | 0.035 | 0.028 | 0.027 | 0.023 | 0.025 | 0.022
| 27 | 0.03 | 0.024 | 0.024 | 0.023 | 0.027 | 0.027
| 28 | 0.027 | 0.025 | 0.027 | 0.026 | 0.029 | 0.029
| 29 | 0.029 | 0.029 | 0.027 | 0.029 | 0.027 | 0.029
| 30 | 0.03 | 0.029 | 0.035 | 0.032 | 0.029 | 0.033
31
Required monitoring frequency:
If continuous, did equipment failure require grab sampling for more than 5 working days?
Total number of analyses: | 179 |  | Number of analyses that exceeded the performance standard 1: |  |  |  |  | 0
Percentage of analyses that exceeded the performance standard 1: |  |  |  |  | 0 | %
Did any analyses exceed the maximum turbidity standard 2? …………………………………………………..
Individual Filter Effluent Turbidity Monitoring (Complete if filtration type is conventional or direct)
Was individual filter effluent turbidity monitoring conducted during the last month?
Did failure of continuous monitoring equipment require grab sampling for more than 5 working days?
Comments:
1 Performance Standards: 0.3 NTU for conventional and direct filtration; 1.0 NTU for slow sand and D.E.; 1.0 NTU or value set by the Department for
alternative filtration
2 Maximum allowable turbidity standards: 1 NTU for conventional and direct filtration; 5 NTU for slow sand and D.E.;5 NTU or value set by the Department
for alternative filtration.
DOH-4303 (1/05) Page 2 of 3

## DOH4303-3
INDIVIDUAL FILTER EFFLUENT TURBIDITY MONITORING
Instructions: Complete this page and attach it to your operation report if you utilize conventional or direct filtration and can answer "YES" to any of
the four questions below.
1. Did any filter(s) exceed 1.0 NTU in two consecutive readings taken 15 minutes apart? ………………………………………………….
If yes report the filter number(s), corresponding date(s), and the turbidity value(s) which exceeded 1.0 NTU during the
month (only for filters that had two consecutive readings exceeding 1.0 NTU), and the reason for abnormal filter
performance. If an obvious reason cannot be identified, a filter profile must be submitted within 7 days of exceedance.
| Filter Number: |  |  |  | Filter Number: |  |  | Filter Number:
| Date | Time | (NTU) |  | Date | Time | (NTU) | Date | Time | (NTU)
2. Did any filter exceed 1.0 NTU in two consecutive readings taken 15 minutes apart at any time
in each of the last 3 consecutive months? ………………………………………………………………
If "YES" a self-assessment of the filter must be conducted by the system. The system should conduct the assessment within 14 days of the exceedance and submit
the self-assessment to the Department. Report the filter number, the date the self-assessment was triggered, and the date it was completed.
Filter Number: |  |  |  | Trigger date: |  |  |  | Completion date:
3. Did any filter exceed 2.0 NTU in two consecutive readings taken 15 minutes apart at any time
in each of the last 2 consecutive months? ……………………………………………………………
If yes a Comprehensive Performance Evaluation (CPE) is required. A copy of the CPE report must be submitted to the Department within 120 days of the trigger date.
Report the filter number that triggered CPE, and the date the CPE was triggered.
Filter Number: |  |  |  | Trigger date:
4. If the system serves > 10,000 persons, did any filter exceed 0.5 NTU in each of the first 2 consecutive
15 minute readings following the first 4 hours of continuous filter operation? ……................
If YES report the filter number, the date on which the exceedance occurred, and the turbidities of the 2 consecutive readings. Report the obvious reason for the abnormal
filter performance, or submit a filter profile within 7 days of the exceedance.
Filter Number: |  |  | Date: |  |  | Consecutive Readings: |  |  | NTU and: |  | NTU
Reason for abnormal filter performance:
Public Water System ID: NY |  |  | 5903442
Reported by (print name): |  |  | John M. Young |  |  |  |  | Title: | Chief Operator
NYSDOH Operator Certification Number:NY |  |  |  |  | 32778 |  |  | Operator Grade Level: |  | IA
Signature: | [7 empty] | Date:
DOH-4303 (1/05) Page 3 of 3

## DOH-360CFL-1
New York State Department of Health | [7 empty] | WATER SYSTEM OPERATION REPORT
Bureau of Water Supply Protection | [7 empty] | For Use By Public Water Systems that Treat with Chlorine and/or Fluoride
Public Water System Name |  |  |  | Reporting Month/Year |  |  |  |  | Date Report Submitted |  |  | Source Water Type(s)
New Castle Consolidate WD |  |  |  | 2023-04-01
Public Water System ID |  |  |  | County |  |  |  |  | Town, Village or City
NY 5903442 |  |  |  | Westchester |  |  |  |  | Millwood
Treatment Plant(s) Identification : |  |  | #1 | [5 empty] | #2 |  |  | #3
Fluoride Compound Used:
Fluoride Residual Testing Method Used: |  |  |  | SPADNS
Fluoride Injection Point Location(s) Id: |  |  | #1 | [5 empty] | #2 |  |  | #3 | Pump Station
Date of Fluoride Split Sample:
DATE | Source(s) in use | Treated Water Volume (1,000/GPD.) |  | Chlorination | [6 empty] | Fluoridation |  |  | Other Treatments
|  |  |  | Gaseous |  |  |  |  | Liquid | Free chlorine residual at entry point (mg/l) | Fluoride Usage per day (gallons) | Fluoride Compound used per day (lbs) | Fluoride finished water (mgL) | Ortho-phosphate Gallons | Potassium Permanganate Lbs/day
|  |  |  | #1 Cylinder weight (lbs.) | #2 Cylinder weight (lbs.) | #3 Cylinder weight (lbs.) | #4 Cylinder weight (lbs.) | Chlorine used per day (lbs.) | Hypochlorite added to crock (gallons or quarts)
1 | Catskill Aqu. | 2224 |  | 0 | 150 | 150 | 150 | 32 |  | 1.2583 |  | 11.555 | 0.715 |  | 0
2 | Catskill Aqu. | 2191 |  | 0 | 150 | 150 | 150 | 24.2 |  | 1.2033 |  | 13.866 | 0.69333 | 6 | 0
3 | Catskill Aqu. | 2165 |  | 0 | 94.8 | 150 | 150 | 27.8 |  | 1.2517 |  | 13.866 | 0.70833 | 6 | 0
4 | Catskill Aqu. | 2209 |  | 0 | 67 | 150 | 150 | 21.8 |  | 1.265 |  | 13.866 | 0.70667 | 7 | 0
5 | Catskill Aqu. | 2229 |  | 0 | 45.2 | 150 | 150 | 27.8 |  | 1.2433 |  | 13.866 | 0.73 | 6 | 0
6 | Catskill Aqu. | 2228 |  | 0 | 17.4 | 150 | 150 | 17.4 |  | 1.2533 |  | 13.866 | 0.73833 | 7 | 0
7 | Catskill Aqu. | 2315 |  | 150 | 150 | 150 | 150 | 31.8 |  | 1.2 |  | 16.177 | 0.71167 | 7 | 0
8 | Catskill Aqu. | 2458 |  | 150 | 150 | 118.2 | 150 | 28.2 |  | 1.2433 |  | 16.177 | 0.74333 | 7 | 0
9 | Catskill Aqu. | 2406 |  | 150 | 150 | 90 | 150 | 27 |  | 1.2633 |  | 16.177 | 0.745 | 8 | 0
10 | Catskill Aqu. | 2912 |  | 150 | 150 | 63 | 150 | 34 |  | 1.2817 |  | 18.488 | 0.74333 | 8 | 0
11 | Catskill Aqu. | 2395 |  | 150 | 150 | 29 | 150 | 26.6 |  | 1.214 |  | 16.177 | 0.734 | 8 | 0
12 | Catskill Aqu. | 3329 |  | 150 | 150 | 2.4 | 150 | 48.2 |  | 1.22 |  | 20.799 | 0.76333 | 10 | 0
13 | Catskill Aqu. | 3021 |  | 150 | 150 | 0 | 104.2 | 34.4 |  | 1.26 |  | 18.488 | 0.77667 | 9 | 0
14 | Catskill Aqu. | 3873 |  | 150 | 150 | 0 | 69.8 | 43.6 |  | 1.285 |  | 23.11 | 0.78833 | 11 | 0
15 | Catskill Aqu. | 2614 |  | 150 | 150 | 0 | 26.2 | 30.2 |  | 1.2433 |  | 16.177 | 0.74333 | 7 | 0
16 | Catskill Aqu. | 2680 |  | 150 | 150 | 0 | 0 | 22.6 |  | 1.2517 |  | 52.2286 | 0.745 | 8 | 0
17 | Catskill Aqu. | 3106 |  | 127.4 | 150 | 0 | 0 | 35.2 |  | 1.28 |  | 17.3325 | 0.725 | 8 | 0
18 | Catskill Aqu. | 2759 |  | 92.2 | 150 | 0 | 0 | 36 |  | 1.2967 |  | 18.488 | 0.72833 | 90 | 0
19 | Catskill Aqu. | 2820 |  | 56.2 | 150 | 0 | 0 | 36.2 |  | 1.26 |  | 20.799 | 0.73333 | 8 | 0
20 | Catskill Aqu. | 3252 |  | 20 | 150 | 0 | 0 | 28.6 |  | 1.2883 |  | 20.799 | 0.75667 | 8 | 0
21 | Catskill Aqu. | 3463 |  | 0 | 141.4 | 0 | 0 | 50.8 |  | 1.2033 |  | 25.421 | 0.75833 | 11 | 0
22 | Catskill Aqu. | 3481 |  | 0 | 90.6 | 150 | 150 | 30.4 |  | 1.2367 |  | 18.488 | 0.76167 | 8 | 0
23 | Catskill Aqu. | 2167 |  | 0 | 60.2 | 150 | 150 | 28.8 |  | 1.26 |  | 16.177 | 0.775 | 7 | 0
24 | Catskill Aqu. | 3133 |  | 0 | 31.4 | 150 | 150 | 44.2 |  | 1.275 |  | 23.11 | 0.8 | 10 | 0
25 | Catskill Aqu. | 3056 |  | 0 | 0 | 137.2 | 150 | 22.2 |  | 1.15 |  | 18.488 | 0.59833 | 7 | 0
26 | Catskill Aqu. | 2749 |  | 0 | 0 | 115 | 150 | 28.4 |  | 1.3 |  | 20.799 | 0.77333 | 7.5 | 0
27 | Catskill Aqu. | 2786 |  | 0 | 0 | 86.6 | 150 | 28.4 |  | 1.16 |  | 20.799 | 0.76667 | 7.5 | 0
28 | Catskill Aqu. | 2747 |  | 0 | 0 | 58.2 | 150 | 26.2 |  | 1.225 |  | 21.9545 | 0.72833 | 7.5 | 0
29 | Catskill Aqu. | 2341 |  | 150 | 150 | 32 | 150 | 22 |  | 1.1833 |  | 16.177 | 0.66167 | 6 | 0
30 | Catskill Aqu. | -14380567 |  | 150 | 150 | 10 | 150 | 26.2 |  | 1.2367 |  | 17.3325 | 0.73 | 8.5 | 0
31 | Catskill Aqu. | 14382935 | [9 empty] | 0 |  |  | 0
Total |  | 81477 | [5 empty] | 921.2 |  |  |  | 571.0481 |  | 309
Average |  | 2628.2903 | [5 empty] | 30.7067 |  | 1.2431 |  | 18.4209 | 0.73608 | 10.6552
Chlorine Mix Ration = |  |  |  | quarts/gallons of | [5 empty] | %chlorine added to |  |  | gallons of water in crock
Reported by/Title: |  | John M. Young, Chief Operator | [7 empty] | NYSDOH Operator Certification Number |  |  |  | 32778
Signature: | [8 empty] | Date: |  |  | Operator Grade Level: |  |  | IA
DOH-360CFL (Rev. 10/04) page 1 of 2

## DOH-360CFL-2
Microbiological Samples and Free Chlorine Residual
Sample Location | Date of Sample | Sample Type | Total Coliform Positive |  | E-coli Positive | Free Chlorine Residual (mg/l) | Population Served: |  | 16800
[7 empty] | # of microbiological monitoring samples required: |  |  | 15
|  | 1. Routine 2. Repeat |  |  |  |  | Number of microbiological monitoring samples taken: |  |  | 16
Did an M&R violation occur?
If "Yes," Check Reason(s) below:
Did an MCL violation occur?
If "Yes," check reason(s) below (see also Part 5, Table 6 for Additional information)
Sample Collector | Town of New Castel DPW | [6 empty] | Date: | 5-5-22 - 5-31-22
Sample Collector | [7 empty] | Date:
Name of NYSDOH Certified Laboratory: |  |  |  | Westchester County Deparment of Labs and Research
Did any MCL violation occur? If so, please describe:
Did an emergency or low pressure problem occur?
Did source water bypass an existing treatment process in the system? | [7 empty] | If so, please explain:
Comments:
DOH-360CFL (Rev. 10/04) page 2 of 2